## blocks
did | device_type | device_name | block_name | block_length | field_name | command_name | start | end | offset | size | type | rw | unit | scale_factor | values | aliases | write_active | min | max
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_DID |  | 1 | 1 | 0 | 1 | uint16 | R |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Length |  | 2 | 2 | 1 | 1 | uint16 | R | Registers |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Major_Firmware_Number |  | 3 | 3 | 2 | 1 | uint16 | R |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Mid_Firmware_Number |  | 4 | 4 | 3 | 1 | uint16 | R |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Minor_Firmware_Number |  | 5 | 6 | 4 | 1 | uint16 | R |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Encryption_Key |  | 6 | 6 | 5 | 1 | uint16 | R |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_MAC_Address |  | 7 | 13 | 6 | 7 | string (14) | R |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Write_Password |  | 14 | 21 | 13 | 8 | string (16) | W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Enable_DHCP | system_enable_dhcp | 22 | 22 | 21 | 1 | uint16 | R/W | Enumerated |  | {"0":"DHCP Disabled, use configured network parameter","1":"DHCP Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_TCP/IP_Address | system_tcp_ip_address | 23 | 24 | 22 | 2 | uint32 | R/W | Address |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_TCP/IP_Gateway_MSW | system_tcp_ip_gateway_msw | 25 | 26 | 24 | 2 | uint32 | R/W | Address |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_TCP/IP_Netmask_MSW | system_tcp_ip_netmask_msw | 27 | 28 | 26 | 2 | uint32 | R/W | Address |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_TCP/IP_DNS_1_MSW | system_tcp_ip_dns_1_msw | 29 | 30 | 28 | 2 | uint32 | R/W | Address |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_TCP/IP_DNS_2_MSW | system_tcp_ip_dns_2_msw | 31 | 32 | 30 | 2 | uint32 | R/W | Address |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Modbus_Port | system_modbus_port | 33 | 33 | 32 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_SMTP_Server_Name | system_smtp_server_name | 34 | 53 | 33 | 20 | string (40) | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_SMTP_Account_Name | system_smtp_account_name | 54 | 69 | 53 | 16 | string (32) | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_SMTP_SSL_Enable | system_smtp_ssl_enable | 70 | 70 | 69 | 1 | uint16 | R/W | Enumerated |  | {"0":"SSL Disabled","1":"SSL Enabled (not implemented)"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_SMTP_Email_Password |  | 71 | 78 | 70 | 8 | string 16) | W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_SMTP_Email_User_Name | system_smtp_email_user_name | 79 | 98 | 78 | 20 | string (40) | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Status_Email_Interval | system_status_email_interval | 99 | 99 | 98 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Status_Email_Status_Time | system_status_email_status_time | 100 | 100 | 99 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Status_Email_Subject_Line | system_status_email_subject_line | 101 | 125 | 100 | 25 | string (50) | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Status_Email_To_Address_1 | system_status_email_to_address_1 | 126 | 145 | 125 | 20 | string (40) | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Status_Email_To_Address_2 | system_status_email_to_address_2 | 146 | 165 | 145 | 20 | string (40) | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Alarm_Email_Enable | system_alarm_email_enable | 166 | 166 | 165 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Alarm_Email_Subject_Line | system_alarm_email_subject_line | 167 | 191 | 166 | 25 | string (50) | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Alarm_Email_To_Address_1 | system_alarm_email_to_address_1 | 192 | 211 | 191 | 20 | string (40) | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Alarm_Email_To_Address_2 | system_alarm_email_to_address_2 | 212 | 231 | 211 | 20 | string (40) | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_FTP_Password |  | 232 | 239 | 231 | 8 | string (16) | W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Telnet_Password |  | 240 | 247 | 239 | 8 | string (16) | W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_SD_Card_Data_Log_Write_Interval | system_sd_card_data_log_write_interval | 248 | 248 | 247 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_SD_Card_Data_Log_Retain_Days | system_sd_card_data_log_retain_days | 249 | 249 | 248 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_SD_Card_Data_Logging_Mode | system_sd_card_data_logging_mode | 250 | 250 | 249 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Excel Format","2":"Compact Format"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Time_Server_Name | system_time_server_name | 251 | 270 | 250 | 20 | string (40) | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Enable_Time_Server | system_enable_time_server | 271 | 271 | 270 | 1 | uint16 | R/W | Enumerated |  | {"0":"Time Server Disabled, use configured time parameters","1":"Time Server Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Set_Time_Zone | system_time_zone | 272 | 272 | 271 | 1 | int16 | R/W | Hours |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Enable_Float_Coordination | system_enable_float_coordination | 273 | 273 | 272 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Enable_FNDC_Charge_Termination | system_enable_fndc_charge_termination | 274 | 274 | 273 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Enable_FNDC_Grid_Tie_Control | system_enable_fndc_grid_tie_control | 275 | 275 | 274 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Voltage_SF |  | 276 | 276 | 275 | 1 | int16 | R |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Hour_SF |  | 277 | 277 | 276 | 1 | int16 | R |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Mode | system_ags_mode | 278 | 278 | 277 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Port | system_ags_port | 279 | 279 | 278 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Port_Type | system_ags_port_type | 280 | 280 | 279 | 1 | uint16 | R/W | Enumerated |  | {"0":"Radian AUX Relay","1":"Radian AUX Output"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Generator_Type | system_ags_generator_type | 281 | 281 | 280 | 1 | uint16 | R/W | Enumerated |  | {"0":"AC Gen","1":"DC Gen","2":"No Gen"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_DC_Gen_Absorb_Voltage | system_ags_dc_gen_absorb_voltage | 282 | 282 | 281 | 1 | uint16 | R/W | Volts | OutBack_Voltage_SF |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_DC_Gen_Absorb_Time | system_ags_dc_gen_absorb_time | 283 | 283 | 282 | 1 | uint16 | R/W | Hour | OutBack_Hour_SF |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Fault_Time | system_ags_fault_time | 284 | 284 | 283 | 1 | uint16 | R/W | Minutes |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Gen_Cool_Down_Time | system_ags_gen_cool_down_time | 285 | 285 | 284 | 1 | uint16 | R/W | Minutes |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Gen_Warm_Up_Time | system_ags_gen_warm_up_time | 286 | 286 | 285 | 1 | uint16 | R/W | Minutes |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Generator_Exercise_Mode | system_ags_generator_exercise_mode | 287 | 287 | 286 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Exercise_Start_Hour | system_ags_exercise_start_hour | 288 | 288 | 287 | 1 | uint16 | R/W | Hour |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Exercise_Start_Minute | system_ags_exercise_start_minute | 289 | 289 | 288 | 1 | uint16 | R/W | Minutes |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Exercise_Day | system_ags_exercise_day | 290 | 290 | 289 | 1 | uint16 | R/W | Enumerated |  | {"0":"Sun","1":"Mon","2":"Tue","3":"Wed","4":"Thr","5":"Fri","6":"Sat"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Exercise_Period | system_ags_exercise_period | 291 | 291 | 290 | 1 | uint16 | R/W | Minutes |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Exercise_Interval | system_ags_exercise_interval | 292 | 292 | 291 | 1 | uint16 | R/W | Weeks |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Sell_Mode | system_ags_sell_mode | 293 | 293 | 292 | 1 | uint16 | R/W | Enumerated |  | {"0":"Selling Enabled","1":"Selling Disabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_2_Min_Start_Mode | system_ags_2_min_start_mode | 294 | 294 | 293 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_2_Min_Start_Voltage | system_ags_2_min_start_voltage | 295 | 295 | 294 | 1 | uint16 | R/W | Volts | OutBack_Voltage_SF |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_2_Hour_Start_Mode | system_ags_2_hour_start_mode | 296 | 296 | 295 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_2_Hour_Start_Voltage | system_ags_2_hour_start_voltage | 297 | 297 | 296 | 1 | uint16 | R/W | Volts | OutBack_Voltage_SF |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_24_Hour_Start_Mode | system_ags_24_hour_start_mode | 298 | 298 | 297 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_24_Hour_Start_Voltage | system_ags_24_hour_start_voltage | 299 | 299 | 298 | 1 | uint16 | R/W | Volts | OutBack_Voltage_SF |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Load_Start_Mode | system_ags_load_start_mode | 300 | 300 | 299 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Load_Start_kW | system_ags_load_start_kw | 301 | 301 | 300 | 1 | uint16 | R/W | kWatts |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Load_Start_Delay | system_ags_load_start_delay | 302 | 302 | 301 | 1 | uint16 | R/W | Minutes |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Load_Stop_kW | system_ags_load_stop_kw | 303 | 303 | 302 | 1 | uint16 | R/W | kWatts |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Load_Stop_Delay | system_ags_load_stop_delay | 304 | 304 | 303 | 1 | uint16 | R/W | Minutes |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_SOC_Start_Mode | system_ags_soc_start_mode | 305 | 305 | 304 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_SOC_Start_Percentage | system_ags_soc_start_percentage | 306 | 306 | 305 | 1 | uint16 | R/W | Percent |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_SOC_Stop_Percentage | system_ags_soc_stop_percentage | 307 | 307 | 306 | 1 | uint16 | R/W | Percent |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Enable_Full_Charge_Mode | system_ags_enable_full_charge_mode | 308 | 308 | 307 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Full_Charge_Interval | system_ags_full_charge_interval | 309 | 309 | 308 | 1 | uint16 | R/W | Days |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Must_Run_Mode | system_ags_must_run_mode | 310 | 310 | 309 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Must_Run_Weekday_Start_Hour | system_ags_must_run_weekday_start_hour | 311 | 311 | 310 | 1 | uint16 | R/W | Hour |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Must_Run_Weekday_Start_Minute | system_ags_must_run_weekday_start_minute | 312 | 312 | 311 | 1 | uint16 | R/W | Minute |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Must_Run_Weekday_Stop_Hour | system_ags_must_run_weekday_stop_hour | 313 | 313 | 312 | 1 | uint16 | R/W | Hour |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Must_Run_Weekday_Stop_Minute | system_ags_must_run_weekday_stop_minute | 314 | 314 | 313 | 1 | uint16 | R/W | Minute |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Must_Run_Weekend_Start_Hour | system_ags_must_run_weekend_start_hour | 315 | 315 | 314 | 1 | uint16 | R/W | Hour |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Must_Run_Weekend_Start_Minute | system_ags_must_run_weekend_start_minute | 316 | 316 | 315 | 1 | uint16 | R/W | Minute |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Must_Run_Weekend_Stop_Hour | system_ags_must_run_weekend_stop_hour | 317 | 317 | 316 | 1 | uint16 | R/W | Hour |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Must_Run_Weekend_Stop_Minute | system_ags_must_run_weekend_stop_minute | 318 | 318 | 317 | 1 | uint16 | R/W | Minute |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Quiet_Time_Mode | system_ags_quiet_time_mode | 319 | 319 | 318 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Quiet_Time_Weekday_Start_Hour | system_ags_quiet_time_weekday_start_hour | 320 | 320 | 319 | 1 | uint16 | R/W | Hour |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Quiet_Time_Weekday_Start_Minute | system_ags_quiet_time_weekday_start_minute | 321 | 321 | 320 | 1 | uint16 | R/W | Minute |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Quiet_Time_Weekday_Stop_Hour | system_ags_quiet_time_weekday_stop_hour | 322 | 322 | 321 | 1 | uint16 | R/W | Hour |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Quiet_Time_Weekday_Stop_Minute | system_ags_quiet_time_weekday_stop_minute | 323 | 323 | 322 | 1 | uint16 | R/W | Minute |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Quiet_Time_Weekend_Start_Hour | system_ags_quiet_time_weekend_start_hour | 324 | 324 | 323 | 1 | uint16 | R/W | Hour |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Quiet_Time_Weekend_Start_Minute | system_ags_quiet_time_weekend_start_minute | 325 | 325 | 324 | 1 | uint16 | R/W | Minute |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Quiet_Time_Weekend_Stop_Hour | system_ags_quiet_time_weekend_stop_hour | 326 | 326 | 325 | 1 | uint16 | R/W | Hour |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Quiet_Time_Weekend_Stop_Minute | system_ags_quiet_time_weekend_stop_minute | 327 | 327 | 326 | 1 | uint16 | R/W | Minute |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_Total_Generator_Run_Time | system_ags_total_generator_run_time | 328 | 329 | 327 | 2 | uint32 | R/W | Hours |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_HBX_Mode | system_hbx_mode | 330 | 330 | 329 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Voltage Only","2":"SOC Only","3":"Both"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_HBX_Grid_Connect_Voltage | system_hbx_grid_connect_voltage | 331 | 331 | 330 | 1 | uint16 | R/W | Volts | OutBack_Voltage_SF |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_HBX_Grid_Connect_Delay | system_hbx_grid_connect_delay | 332 | 332 | 331 | 1 | uint16 | R/W | Hours | OutBack_Hour_SF |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_HBX_Grid_Disconnect_Voltage | system_hbx_grid_disconnect_voltage | 333 | 333 | 332 | 1 | uint16 | R/W | Volts | OutBack_Voltage_SF |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_HBX_Grid_Disconnect_Delay | system_hbx_grid_disconnect_delay | 334 | 334 | 333 | 1 | uint16 | R/W | Hours | OutBack_Hour_SF |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_HBX_Grid_Connect_SOC | system_hbx_grid_connect_soc | 335 | 335 | 334 | 1 | uint16 | R/W | Percent |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_HBX_Grid_Disconnect_SOC | system_hbx_grid_disconnect_soc | 336 | 336 | 335 | 1 | uint16 | R/W | Percent |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_1_Mode | system_grid_use_interval_1_mode | 337 | 337 | 336 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_1_Weekday_Start_Hour | system_grid_use_interval_1_weekday_start_hour | 338 | 338 | 337 | 1 | uint16 | R/W | Hour |  |  |  | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_1_Weekday_Start_Minute | system_grid_use_interval_1_weekday_start_minute | 339 | 339 | 338 | 1 | uint16 | R/W | Hour |  |  |  | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_1_Weekday_Stop_Hour | system_grid_use_interval_1_weekday_stop_hour | 340 | 340 | 339 | 1 | uint16 | R/W | Hour |  |  |  | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_1_Weekday_Stop_Minute | system_grid_use_interval_1_weekday_stop_minute | 341 | 341 | 340 | 1 | uint16 | R/W | Hour |  |  |  | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_1_Weekend_Start_Hour | system_grid_use_interval_1_weekend_start_hour | 342 | 342 | 341 | 1 | uint16 | R/W | Hour |  |  |  | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_1_Weekend_Start_Minute | system_grid_use_interval_1_weekend_start_minute | 343 | 343 | 342 | 1 | uint16 | R/W | Hour |  |  |  | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_1_Weekend_Stop_Hour | system_grid_use_interval_1_weekend_stop_hour | 344 | 344 | 343 | 1 | uint16 | R/W | Hour |  |  |  | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_1_Weekend_Stop_Minute | system_grid_use_interval_1_weekend_stop_minute | 345 | 345 | 344 | 1 | uint16 | R/W | Hour |  |  |  | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_2_Mode | system_grid_use_interval_2_mode | 346 | 346 | 345 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_2_Weekday_Start_Hour | system_grid_use_interval_2_weekday_start_hour | 347 | 347 | 346 | 1 | uint16 | R/W | Hour |  |  |  | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_2_Weekday_Start_Minute | system_grid_use_interval_2_weekday_start_minute | 348 | 348 | 347 | 1 | uint16 | R/W | Hour |  |  |  | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_2_Weekday_Stop_Hour | system_grid_use_interval_2_weekday_stop_hour | 349 | 349 | 348 | 1 | uint16 | R/W | Hour |  |  |  | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_2_Weekday_Stop_Minute | system_grid_use_interval_2_weekday_stop_minute | 350 | 350 | 349 | 1 | uint16 | R/W | Hour |  |  |  | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_3_Mode | system_grid_use_interval_3_mode | 351 | 351 | 350 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_3_Weekday_Start_Hour | system_grid_use_interval_3_weekday_start_hour | 352 | 352 | 351 | 1 | uint16 | R/W | Hour |  |  |  | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_3_Weekday_Start_Minute | system_grid_use_interval_3_weekday_start_minute | 353 | 353 | 352 | 1 | uint16 | R/W | Hour |  |  |  | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_3_Weekday_Stop_Hour | system_grid_use_interval_3_weekday_stop_hour | 354 | 354 | 353 | 1 | uint16 | R/W | Hour |  |  |  | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Grid_Use_Interval_3_Weekday_Stop_Minute | system_grid_use_interval_3_weekday_stop_minute | 355 | 355 | 354 | 1 | uint16 | R/W | Hour |  |  |  | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Load_Grid_Transfer_Mode | system_load_grid_transfer_mode | 356 | 356 | 355 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Load_Grid_Transfer_Threshold | system_load_grid_transfer_threshold | 357 | 357 | 356 | 1 | uint16 | R/W | kWatts | OutBack_Voltage_SF |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Load_Grid_Transfer_Connect_Delay | system_load_grid_transfer_connect_delay | 358 | 358 | 357 | 1 | uint16 | R/W | Seconds |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Load_Grid_Transfer_Disconnect_Delay | system_load_grid_transfer_disconnect_delay | 359 | 359 | 358 | 1 | uint16 | R/W | Seconds |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Load_Grid_Transfer_Connect_Battery_Voltage | system_load_grid_transfer_connect_battery_voltage | 360 | 360 | 359 | 1 | uint16 | R/W | Volts | OutBack_Voltage_SF |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Load_Grid_Transfer_Re_Connect_Battery_Voltage | system_load_grid_transfer_re_connect_battery_voltage | 361 | 361 | 360 | 1 | uint16 | R/W | Volts | OutBack_Voltage_SF |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Global_Charger_Control_Mode | system_global_charger_control_mode | 362 | 362 | 361 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Global_Charger_Control_Output_Limit | system_global_charger_control_output_limit | 363 | 363 | 362 | 1 | uint16 | R/W | Amps |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Radian_AC_Coupled_Control_Mode | system_radian_ac_coupled_control_mode | 364 | 364 | 363 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Radian_AC_Coupled_AUX_Port | system_radian_ac_coupled_aux_port | 365 | 365 | 364 | 1 | uint16 | R/W | Port |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_URL_Update_Lock |  | 366 | 367 | 365 | 2 | uint32 | W | key |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Web_Reporting_Base_URL | system_web_reporting_base_url | 368 | 387 | 367 | 20 | string (40) | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_WEB_User_Logged_In_Status | system_web_user_logged_in_status | 388 | 388 | 387 | 1 | uint16 | R/W | Enumerated |  | {"0":"WEB User NOT logged in","1":"WEB user logged in"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_HUB_Type |  | 389 | 389 | 388 | 1 | uint16 | R | Enumerated |  | {"0":"Legacy HUB","4":"HUB4","10":"HUB10.3","11":"HUB3PH"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_HUB_Major_Firmware_Number |  | 390 | 390 | 389 | 1 | uint16 | R |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_HUB_Mid_Firmware_Number |  | 391 | 391 | 390 | 1 | uint16 | R |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_HUB_Minor_Firmware_Number |  | 392 | 392 | 391 | 1 | uint16 | R |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Year | system_year | 393 | 393 | 392 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | Outback_Month | system_outback_month | 394 | 394 | 393 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Day | system_day | 395 | 395 | 394 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Hour | system_hour | 396 | 396 | 395 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | Outback_Minute | system_outback_minute | 397 | 397 | 396 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Second | system_second | 398 | 398 | 397 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Temp_Batt |  | 399 | 399 | 398 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Temp_Ambient |  | 400 | 400 | 399 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Temp_SF |  | 401 | 401 | 400 | 1 | int16 | R |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Error |  | 402 | 402 | 401 | 1 | uint16 | R | Bitfield |  | {"0x0001":"High limit last write","0x0002":"Low limit last write","0x0004":"Last write invalid","0x0008":"DHCP failed","0x0010":"DNS resolve failure","0x0020":"SMTP authorization failed","0x0040":"SMTP send failed","0x0080":"FTP Error","0x0100":"SD-Card Error","0x0200":"SNTP failure","0x0400":"Write while locked","0x0800":"Device firmware updating not supported","0x1000":"Device firmware update file not found","0x2000":"Device firmware update file invalid","0x4000":"Device firmware update failure"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Status |  | 403 | 403 | 402 | 1 | uint16 | R | Bitfield |  | {"0x0001":"Firmware update complete"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Update_Device_Firmware_Port | system_update_device_firmware_port | 404 | 404 | 403 | 1 | uint16 | R/W | Bitfield |  | {"0xPPXX":["XX = device port number to update: 0-10","PP = FW Update percent complete 0-100%"]} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Gateway_Type |  | 405 | 405 | 404 | 1 | uint16 | R | Enumerated |  | {"1":"AXS Port","2":"MATE3"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_System_Voltage |  | 406 | 406 | 405 | 1 | uint16 | R | Volts |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Measured_System_Voltage |  | 407 | 407 | 406 | 1 | uint16 | R | Volts | OutBack_Voltage_SF |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_AGS_AC_Reconnect_Delay | system_ags_ac_reconnect_delay | 408 | 408 | 407 | 1 | uint16 | R/W | Minute |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Multi_Phase_Coordination | system_multi_phase_coordination | 409 | 409 | 408 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Sched_1_AC_Mode | system_sched_1_ac_mode | 410 | 410 | 409 | 1 | int16 | R/W | Enumerated |  | {"-1":"Disable","0":"Generator","1":"Support","2":"Grid Tied","3":"UPS","4":"Backup","5":"Mini Grid","6":"Grid Zero"} | {"-1":"Disabled","0":"Generator","1":"Support","2":"GridTied","3":"UPS","4":"Backup","5":"MiniGrid","6":"GridZero"} | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Sched_1_AC_Mode_Hour | system_sched_1_ac_mode_hour | 411 | 411 | 410 | 1 | uint16 | R/W | Hour |  |  |  | TRUE | 0 | 23
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Sched_1_AC_Mode_Minute | system_sched_1_ac_mode_minute | 412 | 412 | 411 | 1 | uint16 | R/W | Minute |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Sched_2_AC_Mode | system_sched_2_ac_mode | 413 | 413 | 412 | 1 | int16 | R/W | Enumerated |  | {"-1":"Disable","0":"Generator","1":"Support","2":"Grid Tied","3":"UPS","4":"Backup","5":"Mini Grid","6":"Grid Zero"} | {"-1":"Disabled","0":"Generator","1":"Support","2":"GridTied","3":"UPS","4":"Backup","5":"MiniGrid","6":"GridZero"} | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Sched_2_AC_Mode_Hour | system_sched_2_ac_mode_hour | 414 | 414 | 413 | 1 | uint16 | R/W | Hour |  |  |  | TRUE | 0 | 23
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Sched_2_AC_Mode_Minute | system_sched_2_ac_mode_minute | 415 | 415 | 414 | 1 | uint16 | R/W | Minute |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Sched_3_AC_Mode | system_sched_3_ac_mode | 416 | 416 | 415 | 1 | int16 | R/W | Enumerated |  | {"-1":"Disable","0":"Generator","1":"Support","2":"Grid Tied","3":"UPS","4":"Backup","5":"Mini Grid","6":"Grid Zero"} | {"-1":"Disabled","0":"Generator","1":"Support","2":"GridTied","3":"UPS","4":"Backup","5":"MiniGrid","6":"GridZero"} | TRUE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Sched_3_AC_Mode_Hour | system_sched_3_ac_mode_hour | 417 | 417 | 416 | 1 | uint16 | R/W | Hour |  |  |  | TRUE | 0 | 23
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Sched_3_AC_Mode_Minute | system_sched_3_ac_mode_minute | 418 | 418 | 417 | 1 | uint16 | R/W | Minute |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Auto_reboot | system_auto_reboot | 419 | 419 | 418 | 1 | uint16 | R/W | Enumerated |  | {"0":"Disable","1":"24","2":"20","3":"16","4":"12","5":"8","6":"4 (hours)"} | {} | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Spare_Reg_2 | system_spare_reg_2 | 420 | 420 | 419 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Spare_Reg_3 | system_spare_reg_3 | 421 | 421 | 420 | 1 | uint16 | R/W |  |  |  |  | FALSE
64110 | system | OutBack Interface | OutBack Block | 420 | OutBack_Spare_Reg_4 | system_spare_reg_4 | 422 | 422 | 421 | 1 | uint16 | R/W |  |  |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_DID |  | 1 | 1 | 0 | 1 | uint16 | R |  |  |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Length |  | 2 | 2 | 1 | 1 | uint16 | R | Registers |  |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Port_number |  | 3 | 3 | 2 | 1 | uint16 | R |  |  |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Voltage_SF |  | 4 | 4 | 3 | 1 | int16 | R |  |  |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Current_SF |  | 5 | 5 | 4 | 1 | int16 | R |  |  |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Power_SF |  | 6 | 6 | 5 | 1 | int16 | R |  |  |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_AH_SF |  | 7 | 7 | 6 | 1 | int16 | R |  |  |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_KWH_SF |  | 8 | 8 | 7 | 1 | int16 | R |  |  |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Batt_Voltage |  | 9 | 9 | 8 | 1 | uint16 | R | Volts | CC_Voltage_SF |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Array_Voltage |  | 10 | 10 | 9 | 1 | uint16 | R | Volts | CC_Voltage_SF |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Batt_Current |  | 11 | 11 | 10 | 1 | uint16 | R | Amps | CC_Current_SF |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Array_Current |  | 12 | 12 | 11 | 1 | uint16 | R | Amps | CC_Power_SF |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Charger_State |  | 13 | 13 | 12 | 1 | uint16 | R | Enumerated |  | {"0":"Silent","1":"Float","2":"Bulk","3":"Absorb","4":"EQ"} | {"0":"Silent","1":"Float","2":"Bulk","3":"Absorb","4":"Equalize"} | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Watts |  | 14 | 14 | 13 | 1 | uint16 | R | Watts | CC_Power_SF |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Todays_Min_Battery_Volts |  | 15 | 15 | 14 | 1 | uint16 | R | Volts | CC_Voltage_SF |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Todays_Max_Battery_Volts |  | 16 | 16 | 15 | 1 | uint16 | R | Volts | CC_Voltage_SF |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_VOC |  | 17 | 17 | 16 | 1 | uint16 | R | Volts | CC_Voltage_SF |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Todays_Peak_VOC |  | 18 | 18 | 17 | 1 | uint16 | R | Volts |  |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Todays_kWH |  | 19 | 19 | 18 | 1 | uint16 | R | KWH | CC_KWH_SF |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Todays_AH |  | 20 | 20 | 19 | 1 | uint16 | R | AH | CC_AH_SF |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Lifetime_kWH_Hours |  | 21 | 21 | 20 | 1 | uint16 | R | KWH |  |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Lifetime_kAmp_Hours |  | 22 | 22 | 21 | 1 | uint16 | R | Amps | CC_KWH_SF |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Lifetime_Max_Watts |  | 23 | 23 | 22 | 1 | uint16 | R | Watts | CC_Power_SF |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Lifetime_Max_Battery_Volts |  | 24 | 24 | 23 | 1 | uint16 | R | Volts | CC_Voltage_SF |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Lifetime_Max_VOC |  | 25 | 25 | 24 | 1 | uint16 | R | Volts | CC_Voltage_SF |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Temp_SF |  | 26 | 26 | 25 | 1 | uint16 | R |  |  |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Temp_Output_FETs |  | 27 | 27 | 26 | 1 | int16 | R | Degrees C | CC_Power_SF |  |  | FALSE
64111 | charger | Charge Controller | Charge Controller Block | 26 | CC_Temp_Enclosure |  | 28 | 28 | 27 | 1 | int16 | R | Degrees C | CC_Power_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_DID |  | 1 | 1 | 0 | 1 | uint16 | R |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Length |  | 2 | 2 | 1 | 1 | uint16 | R | Registers |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Port_number |  | 3 | 3 | 2 | 1 | uint16 | R |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Voltage_SF |  | 4 | 4 | 3 | 1 | int16 | R |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Current_SF |  | 5 | 5 | 4 | 1 | int16 | R |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Hours_SF |  | 6 | 6 | 5 | 1 | int16 | R |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Power_SF |  | 7 | 7 | 6 | 1 | int16 | R |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AH_SF |  | 8 | 8 | 7 | 1 | int16 | R |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_KWH_SF |  | 9 | 9 | 8 | 1 | int16 | R |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Faults |  | 10 | 10 | 9 | 1 | uint16 | R | Bitfield |  | {"0x0080":"High VOC","0x0040":"Over Temp","0x0020":"Shorted Battery Temp Sensor","0x0010":"Fault Input Active"} | {} | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Absorb_Volts | charger_absorb_voltage | 11 | 11 | 10 | 1 | uint16 | R/W | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Absorb_Time_Hours | charger_absorb_time_hours | 12 | 12 | 11 | 1 | uint16 | R/W | Hours | CCconfig_Hours_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Absorb_End_Amps | charger_absorb_end_amps | 13 | 13 | 12 | 1 | uint16 | R/W | Amps |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Rebulk_Volts | charger_rebulk_voltage | 14 | 14 | 13 | 1 | uint16 | R/W | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Float_Volts | charger_float_voltage | 15 | 15 | 14 | 1 | uint16 | R/W | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Bulk_Current | charger_bulk_current | 16 | 16 | 15 | 1 | uint16 | R/W | Amps | CCconfig_Current_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_EQ_Volts | charger_eq_voltage | 17 | 17 | 16 | 1 | uint16 | R/W | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_EQ_Time_Hours | charger_eq_time_hours | 18 | 18 | 17 | 1 | uint16 | R/W | Hours |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Auto_EQ_Days | charger_auto_eq_days | 19 | 19 | 18 | 1 | uint16 | R/W | Days |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_MPPT_Mode | charger_mppt_mode | 20 | 20 | 19 | 1 | uint16 | R/W | Enumerated |  | {"0":"Auto","1":"U-Pick"} | {} | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Sweep_Width | charger_sweep_width | 21 | 21 | 20 | 1 | uint16 | R/W | Enumerated |  | {"0":"Full","1":"Half"} | {} | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Sweep_Max_Percentage | charger_sweep_max_percentage | 22 | 22 | 21 | 1 | uint16 | R/W | Enumerated |  | {"0":"80","1":"85","2":"90","3":"99"} | {} | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_U_Pick_PWM_Duty_Cycle | charger_u_pick_pwm_duty_cycle | 23 | 23 | 22 | 1 | uint16 | R/W | Percentage | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Grid_Tie_Mode | charger_grid_tie_mode | 24 | 24 | 23 | 1 | uint16 | R/W | Enumerated |  | {"0":"Grid Tie Mode disabled","1":"Grid Tie Mode enabled"} | {} | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Temp_Comp_Mode | charger_temp_comp_mode | 25 | 25 | 24 | 1 | uint16 | R/W | Enumerated |  | {"0":"Wide","1":"User Limited"} | {} | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Temp_Comp_Lower_Limit_Volts | charger_temp_comp_lower_limit_voltage | 26 | 26 | 25 | 1 | uint16 | R/W | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Temp_Comp_Upper_Limit_Volts | charger_temp_comp_upper_limit_voltage | 27 | 27 | 26 | 1 | uint16 | R/W | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Temp_Comp_Slope | charger_temp_comp_slope | 28 | 28 | 27 | 1 | uint16 | R/W | Milli Volts |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Auto_Restart_Mode | charger_auto_restart_mode | 29 | 29 | 28 | 1 | uint16 | R/W | Enumerated |  | {"0":"Off","1":"Restart every 90 minutes","2":"Restart every 90 minutes if absorb charging or float charging"} | {} | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Wakeup_VOC | charger_wakeup_voc | 30 | 30 | 29 | 1 | uint16 | R/W | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Snooze_Mode_Amps | charger_snooze_mode_amps | 31 | 31 | 30 | 1 | uint16 | R/W | Amps | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Wakeup_Interval | charger_wakeup_interval | 32 | 32 | 31 | 1 | uint16 | R/W | Mins |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AUX_Mode | charger_aux_mode | 33 | 33 | 32 | 1 | uint16 | R/W | Enumerated |  | {"0":"Float","1":"Diversion: Relay","2":"Diversion: Solid St","3":"Low Batt Disconnect","4":"Remote","5":"Vent Fan","6":"PV Trigger","7":"Error Output","8":"Night Light"} | {"0":"Float","1":"Diversion: Relay","2":"Diversion:SSR","3":"Low Batt Disconnect","4":"Remote","5":"Vent Fan","6":"PV Trigger","7":"Error Output","8":"Night Light"} | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AUX_Control | charger_aux_control | 34 | 34 | 33 | 1 | uint16 | R/W | Enumerated |  | {"0":"Off","1":"Auto","2":"On"} | {"0":"off","1":"auto","2":"on"} | TRUE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AUX_State |  | 35 | 35 | 34 | 1 | uint16 | R | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {"0":"Disabled","1":"Enabled"} | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AUX_Polarity | charger_aux_polarity | 36 | 36 | 35 | 1 | uint16 | R/W | Enumerated |  | {"0":"Low","1":"High"} | {} | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AUX_Low_Batt_Disconnect | charger_aux_low_batt_disconnect | 37 | 37 | 36 | 1 | uint16 | R/W | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AUX_Low_Batt_Reconnect | charger_aux_low_batt_reconnect | 38 | 38 | 37 | 1 | uint16 | R/W | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AUX_Low_Batt_Disconnect_Delay | charger_aux_low_batt_disconnect_delay | 39 | 39 | 38 | 1 | uint16 | R/W | Secs |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AUX_Vent_Fan_Volts | charger_aux_vent_fan_voltage | 40 | 40 | 39 | 1 | uint16 | R/W | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AUX_PV_Limit_Volts | charger_aux_pv_limit_voltage | 41 | 41 | 40 | 1 | uint16 | R/W | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AUX_PV_Limit_Hold_Time | charger_aux_pv_limit_hold_time | 42 | 42 | 41 | 1 | uint16 | R/W | Secs | CCconfig_Hours_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AUX_Night_Light_Thres_Volts | charger_aux_night_light_thres_voltage | 43 | 43 | 42 | 1 | uint16 | R/W | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Night_Light_ON_Hours | charger_night_light_on_hours | 44 | 44 | 43 | 1 | uint16 | R/W | Hours |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Night_Light_ON_Hyst_Time | charger_night_light_on_hyst_time | 45 | 45 | 44 | 1 | uint16 | R/W | Mins |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Night_Light_OFF_Hyst_Time | charger_night_light_off_hyst_time | 46 | 46 | 45 | 1 | uint16 | R/W | Mins |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AUX_Error_Battery_Volts | charger_aux_error_battery_voltage | 47 | 47 | 46 | 1 | uint16 | R/W | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AUX_Divert_Hold_Time | charger_aux_divert_hold_time | 48 | 48 | 47 | 1 | uint16 | R/W | Seconds | CCconfig_Hours_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AUX_Divert_Delay_Time | charger_aux_divert_delay_time | 49 | 49 | 48 | 1 | uint16 | R/W | Secs |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AUX_Divert_Relative_Volts | charger_aux_divert_relative_voltage | 50 | 50 | 49 | 1 | int16 | R/W | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_AUX_Divert_Hyst_Volts | charger_aux_divert_hyst_voltage | 51 | 51 | 50 | 1 | uint16 | R/W | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Major_Firmware_Number |  | 52 | 52 | 51 | 1 | uint16 | R |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Mid_Firmware_Number |  | 53 | 53 | 52 | 1 | uint16 | R |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Minor_Firmware_Number |  | 54 | 54 | 53 | 1 | uint16 | R |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Set_Data_Log_Day_Offset | charger_data_log_day_offset | 55 | 55 | 54 | 1 | uint16 | R/W | Days |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Get_Current_Data_Log_Day_Offset |  | 56 | 56 | 55 | 1 | uint16 | R | Days |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Data_Log_Daily_AH |  | 57 | 57 | 56 | 1 | uint16 | R | AH | CCconfig_AH_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Data_Log_Daily_kWH |  | 58 | 58 | 57 | 1 | uint16 | R | KWH | CCconfig_KWH_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Data_Log_Daily_Max_Output_Amps |  | 59 | 59 | 58 | 1 | uint16 | R | Amps | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Data_Log_Daily_Max_Output_Watts |  | 60 | 60 | 59 | 1 | uint16 | R | Watts | CCconfig_Power_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Data_Log_Daily_Absorb_Time |  | 61 | 61 | 60 | 1 | uint16 | R | Mins |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Data_Log_Daily_Float_Time |  | 62 | 62 | 61 | 1 | uint16 | R | Mins |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Data_Log_Daily_Min_Batt_Volts |  | 63 | 63 | 62 | 1 | uint16 | R | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Data_Log_Daily_Max_Batt_Volts |  | 64 | 64 | 63 | 1 | uint16 | R | Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Data_Log_Daily_Max_Input_Volts |  | 65 | 65 | 64 | 1 | uint16 | R | Volts |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Clear_Data_Log_Read |  | 66 | 66 | 65 | 1 | uint16 | R |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Clear_Data_Log_Write_Complement |  | 67 | 67 | 66 | 1 | uint16 | W |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Stats_Maximum_Reset_Read |  | 68 | 68 | 67 | 1 | uint16 | R |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Stats_Maximum_Write_Complement |  | 69 | 69 | 68 | 1 | uint16 | W |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Stats_Totals_Reset_Read |  | 70 | 70 | 69 | 1 | uint16 | R |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Stats_Totals_Write_Complement |  | 71 | 71 | 70 | 1 | uint16 | W |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Battery_Voltage_Calibrate_Offset | charger_battery_voltage_calibrate_offset | 72 | 72 | 71 | 1 | int16 | R/W | DC Volts | CCconfig_Voltage_SF |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Serial_Number |  | 73 | 81 | 72 | 9 | string (18) | R |  |  |  |  | FALSE
64112 | charger | FM Series Charge Controller | Charge Controller Configuration Block | 88 | CCconfig_Model_Number |  | 82 | 90 | 81 | 9 | string (18) | R |  |  |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_DID |  | 1 | 1 | 0 | 1 | uint16 | R |  |  |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Length |  | 2 | 2 | 1 | 1 | uint16 | R | Registers |  |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Port_number |  | 3 | 3 | 2 | 1 | uint16 | R |  |  |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_DC_Voltage_SF |  | 4 | 4 | 3 | 1 | int16 | R |  |  |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AC_Current_SF |  | 5 | 5 | 4 | 1 | int16 | R |  |  |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AC_Voltage_SF |  | 6 | 6 | 5 | 1 | int16 | R |  |  |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AC_Frequency_SF |  | 7 | 7 | 6 | 1 | int16 | R |  |  |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L1_Inverter_Output_Current |  | 8 | 8 | 7 | 1 | int16 | R | Amps | GS_Split_AC_Current_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L1_Inverter_Charge_Current |  | 9 | 9 | 8 | 1 | int16 | R | Amps | GS_Split_AC_Current_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L1_Inverter_Buy_Current |  | 10 | 10 | 9 | 1 | int16 | R | Amps | GS_Split_AC_Current_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L1_Inverter_Sell_Current |  | 11 | 11 | 10 | 1 | int16 | R | Amps | GS_Split_AC_Current_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L1_Grid_Input_AC_Voltage |  | 12 | 12 | 11 | 1 | int16 | R | Volts AC | GS_Split_AC_Voltage_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L1_Gen_Input_AC_Voltage |  | 13 | 13 | 12 | 1 | int16 | R | Volts AC | GS_Split_AC_Voltage_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L1_Output_AC_Voltage |  | 14 | 14 | 13 | 1 | int16 | R | Volts AC | GS_Split_AC_Voltage_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L2_Inverter_Output_Current |  | 15 | 15 | 14 | 1 | int16 | R | Amps | GS_Split_AC_Current_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L2_Inverter_Charge_Current |  | 16 | 16 | 15 | 1 | int16 | R | Amps | GS_Split_AC_Current_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L2_Inverter_Buy_Current |  | 17 | 17 | 16 | 1 | int16 | R | Amps | GS_Split_AC_Current_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L2_Inverter_Sell_Current |  | 18 | 18 | 17 | 1 | int16 | R | Amps | GS_Split_AC_Current_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L2_Grid_Input_AC_Voltage |  | 19 | 19 | 18 | 1 | int16 | R | Volts AC | GS_Split_AC_Voltage_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L2_Gen_Input_AC_Voltage |  | 20 | 20 | 19 | 1 | int16 | R | Volts AC | GS_Split_AC_Voltage_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L2_Output_AC_Voltage |  | 21 | 21 | 20 | 1 | int16 | R | Volts AC | GS_Split_AC_Voltage_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Inverter_Operating_mode |  | 22 | 22 | 21 | 1 | int16 | R | Enumerated |  | {"0":"Off","1":"Searching","2":"Inverting","3":"Charging","4":"Silent","5":"Float","6":"EQ","7":"Charger Off","8":"Support","9":"Selling","10":"Pass through","14":"Offsetting"} | {"0":"Off","1":"Searching","2":"Inverting","3":"Charging","4":"Silent","5":"Float","6":"Equalize","7":"Charger Off","8":"Support","9":"Sell","10":"Pass-through","11":"Slave Inverter On","12":"Slave Inverter Off","13":"Unknown","14":"Offsetting","15":"AGS Error","16":"Comm Error"} | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Error_Flags |  | 23 | 23 | 22 | 1 | int16 | R | Bitfield |  | {"0x0001":"Low AC output voltage","0x0002":"Stacking error","0x0004":"Over temperature error","0x0008":"Low battery voltage","0x0010":"Phase loss","0x0020":"High battery voltage","0x0040":"AC output shorted","0x0080":"AC backfeed"} | {} | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Warning_Flags |  | 24 | 24 | 23 | 1 | int16 | R | Bitfield |  | {"0x0001":"AC input frequency too high","0x0002":"AC input frequency too low","0x0004":"AC input voltage too low","0x0008":"AC input voltage too high","0x0010":"AC input current exceeds max","0x0020":"Temperature sensor bad","0x0040":"Communications error","0x0080":"Cooling fan fault"} | {} | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Battery_Voltage |  | 25 | 25 | 24 | 1 | int16 | R | Volts DC | GS_Split_DC_Voltage_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Temp_Compensated_Target_Voltage |  | 26 | 26 | 25 | 1 | int16 | R | Volts DC | GS_Split_DC_Voltage_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AUX_Output_State |  | 27 | 27 | 26 | 1 | int16 | R | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AUX_Relay_Output_State |  | 28 | 28 | 27 | 1 | int16 | R | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {"0":"disabled","1":"enabled"} | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L_Module_Transformer_Temperature |  | 29 | 29 | 28 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L_Module_Capacitor_Temperature |  | 30 | 30 | 29 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L_Module_FET_Temperature |  | 31 | 31 | 30 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_R_Module_Transformer_Temperature |  | 32 | 32 | 31 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_R_Module_Capacitor_Temperature |  | 33 | 33 | 32 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_R_Module_FET_Temperature |  | 34 | 34 | 33 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Battery_Temperature |  | 35 | 35 | 34 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AC_Input_Selection |  | 36 | 36 | 35 | 1 | int16 | R | Enumerated |  | {"0":"Grid","1":"Gen"} | {} | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AC_Input_Frequency |  | 37 | 37 | 36 | 1 | int16 | R | Hz | GS_Split_AC_Frequency_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AC_Input_Voltage |  | 38 | 38 | 37 | 1 | int16 | R | Volts AC | GS_Split_AC_Voltage_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AC_Input_State |  | 39 | 39 | 38 | 1 | int16 | R | Enumerated |  | {"1":"AC Use","0":"AC_Drop"} | {"0":"AC Drop","1":"AC Use"} | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Minimum_AC_Input_Voltage |  | 40 | 40 | 39 | 1 | int16 | R | Volts AC | GS_Split_AC_Voltage_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Maximum_AC_Input_Voltage |  | 41 | 41 | 40 | 1 | int16 | R | Volts AC | GS_Split_AC_Voltage_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Sell_Status |  | 42 | 42 | 41 | 1 | int16 | R | Bitfield |  | {"0x0001":"AC input frequency too high","0x0002":"AC input frequency too low","0x0004":"AC input voltage too low","0x0008":"AC input voltage too high","0x0010":"Awaiting sell delay","0x0020":"Sell disabled","0x0040":"Battery voltage less than target"} | {} | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_kWh_SF |  | 43 | 43 | 42 | 1 | int16 | R |  |  |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AC1_L1_Buy_kWh |  | 44 | 44 | 43 | 1 | uint16 | R | kWh | GS_Split_kWh_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AC2_L1_Buy_kWh |  | 45 | 45 | 44 | 1 | uint16 | R | kWh | GS_Split_kWh_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AC1_L1_Sell_kWh |  | 46 | 46 | 45 | 1 | uint16 | R | kWh | GS_Split_kWh_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AC2_L1_Sell_kWh |  | 47 | 47 | 46 | 1 | uint16 | R | kWh | GS_Split_kWh_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L1_Output_kWh |  | 48 | 48 | 47 | 1 | uint16 | R | kWh | GS_Split_kWh_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AC1_L2_Buy_kWh |  | 49 | 49 | 48 | 1 | uint16 | R | kWh | GS_Split_kWh_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AC2_L2_Buy_kWh |  | 50 | 50 | 49 | 1 | uint16 | R | kWh | GS_Split_kWh_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AC1_L2_Sell_kWh |  | 51 | 51 | 50 | 1 | uint16 | R | kWh | GS_Split_kWh_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AC2_L2_Sell_kWh |  | 52 | 52 | 51 | 1 | uint16 | R | kWh | GS_Split_kWh_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_L2_Output_kWh |  | 53 | 53 | 52 | 1 | uint16 | R | kWh | GS_Split_kWh_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Charger_kWh |  | 54 | 54 | 53 | 1 | uint16 | R | kWh | GS_Split_kWh_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Output_kW |  | 55 | 55 | 54 | 1 | uint16 | R | kW | GS_Split_kWh_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Buy_kW |  | 56 | 56 | 55 | 1 | uint16 | R | kW | GS_Split_kWh_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Sell_kW |  | 57 | 57 | 56 | 1 | uint16 | R | kW | GS_Split_kWh_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Charge_kW |  | 58 | 58 | 57 | 1 | uint16 | R | kW | GS_Split_kWh_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_Load_kW |  | 59 | 59 | 58 | 1 | uint16 | R | kW | GS_Split_kWh_SF |  |  | FALSE
64115 | inverter | Radian Split Phase Inverter | Split Phase Radian Inverter Real Time Block | 58 | GS_Split_AC_Couple_kW |  | 60 | 60 | 59 | 1 | uint16 | R | kW | GS_Split_kWh_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_DID |  | 1 | 1 | 0 | 1 | uint16 | R |  |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Length |  | 2 | 2 | 1 | 1 | uint16 | R | Registers |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Port_number |  | 3 | 3 | 2 | 1 | uint16 | R |  |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_DC_Voltage_SF |  | 4 | 4 | 3 | 1 | int16 | R |  |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AC_Current_SF |  | 5 | 5 | 4 | 1 | int16 | R |  |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AC_Voltage_SF |  | 6 | 6 | 5 | 1 | int16 | R |  |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Time_SF |  | 7 | 7 | 6 | 1 | int16 | R |  |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Major_Firmware_Number |  | 8 | 8 | 7 | 1 | uint16 | R |  |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Mid_Firmware_Number |  | 9 | 9 | 8 | 1 | uint16 | R |  |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Minor_Firmware_Number |  | 10 | 10 | 9 | 1 | uint16 | R |  |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Absorb_Volts | inverter_absorb_voltage | 11 | 11 | 10 | 1 | uint16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Absorb_Time_Hours | inverter_absorb_time_hours | 12 | 12 | 11 | 1 | uint16 | R/W | Hours | GSconfig_Time_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Float_Volts | inverter_float_voltage | 13 | 13 | 12 | 1 | uint16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Float_Time_Hours | inverter_float_time_hours | 14 | 14 | 13 | 1 | uint16 | R/W | Hours | GSconfig_Time_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_ReFloat_Volts | inverter_refloat_voltage | 15 | 15 | 14 | 1 | uint16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_EQ_Volts | inverter_eq_voltage | 16 | 16 | 15 | 1 | uint16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_EQ_Time_Hours | inverter_eq_time_hours | 17 | 17 | 16 | 1 | uint16 | R/W | Hours | GSconfig_Time_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Search_Sensitivity | inverter_search_sensitivity | 18 | 18 | 17 | 1 | uint16 | R/W |  |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Search_Pulse_Length | inverter_search_pulse_length | 19 | 19 | 18 | 1 | uint16 | R/W | Cycles |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Search_Pulse_Spacing | inverter_search_pulse_spacing | 20 | 20 | 19 | 1 | uint16 | R/W | Cycles |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AC_Input_Select_Priority | inverter_ac_input_select_priority | 21 | 21 | 20 | 1 | uint16 | R/W | Enumerated |  | {"0":"Grid","1":"Gen"} | {} | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Grid_AC_Input_Current_Limit | inverter_grid_ac_input_current_limit | 22 | 22 | 21 | 1 | uint16 | R/W | Amps | GSconfig_AC_Current_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Gen_AC_Input_Current_Limit | inverter_gen_ac_input_current_limit | 23 | 23 | 22 | 1 | uint16 | R/W | Amps | GSconfig_AC_Current_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Charger_AC_Input_Current_Limit | inverter_charger_ac_input_current_limit | 24 | 24 | 23 | 1 | uint16 | R/W | Amps | GSconfig_AC_Current_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Charger_Operating_Mode | inverter_charger_operating_mode | 25 | 25 | 24 | 1 | uint16 | R/W | Enumerated |  | {"0":"All Inverter Charging Disabled","1":"Bulk and Float Charging Enabled"} | {"0":"Off","1":"On"} | TRUE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AC_Coupled | inverter_ac_coupled | 26 | 26 | 25 | 1 | uint16 | R/W | Enumerated |  | {"0":"No","1":"Yes (not implemented)"} | {} | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Grid_Input_Mode | inverter_grid_input_mode | 27 | 27 | 26 | 1 | uint16 | R/W | Enumerated |  | {"0":"Generator","1":"Support","2":"Grid Tied","3":"UPS","4":"Backup","5":"Mini Grid","6":"Grid Zero"} | {"0":"Generator","1":"Support","2":"GridTied","3":"UPS","4":"Backup","5":"MiniGrid","6":"GridZero"} | TRUE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Grid_Lower_Input_Voltage_Limit | inverter_grid_lower_input_voltage_limit | 28 | 28 | 27 | 1 | uint16 | R/W | Volts AC | GSconfig_AC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Grid_Upper_Input_Voltage_Limit | inverter_grid_upper_input_voltage_limit | 29 | 29 | 28 | 1 | uint16 | R/W | Volts AC | GSconfig_AC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Grid_Transfer_Delay | inverter_grid_transfer_delay | 30 | 30 | 29 | 1 | uint16 | R/W | msecs |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Grid_Connect_Delay | inverter_grid_connect_delay | 31 | 31 | 30 | 1 | uint16 | R/W | Minutes | GSconfig_Time_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Gen_Input_Mode | inverter_gen_input_mode | 32 | 32 | 31 | 1 | uint16 | R/W | Enumerated |  | {"0":"Generator","1":"Support","2":"Grid Tied","3":"UPS","4":"Backup","5":"Mini Grid","6":"Grid Zero"} | {} | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Gen_Lower_Input_Voltage_Limit | inverter_gen_lower_input_voltage_limit | 33 | 33 | 32 | 1 | uint16 | R/W | Volts AC | GSconfig_AC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Gen_Upper_Input_Voltage_Limit | inverter_gen_upper_input_voltage_limit | 34 | 34 | 33 | 1 | uint16 | R/W | Volts AC | GSconfig_AC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Gen_Transfer_Delay | inverter_gen_transfer_delay | 35 | 35 | 34 | 1 | uint16 | R/W | msecs |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Gen_Connect_Delay | inverter_gen_connect_delay | 36 | 36 | 35 | 1 | uint16 | R/W | Minutes | GSconfig_Time_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AC_Output_Voltage | inverter_ac_output_voltage | 37 | 37 | 36 | 1 | uint16 | R/W | Volts AC | GSconfig_AC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Low_Battery_Cut_Out_Voltage | inverter_low_battery_cut_out_voltage | 38 | 38 | 37 | 1 | uint16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Low_Battery_Cut_In_Voltage | inverter_low_battery_cut_in_voltage | 39 | 39 | 38 | 1 | uint16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AUX_Mode | inverter_aux_mode | 40 | 40 | 39 | 1 | uint16 | R/W | Enumerated |  | {"1":"Load Shed","2":"Gen Alert","3":"Fault","4":"Vent Fan","5":"Cool Fan","6":"DC Divert","7":"Grid Limit/IEEE","8":"AC Source Status","9":"AC Divert"} | {} | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AUX_Control | inverter_aux_control | 41 | 41 | 40 | 1 | uint16 | R/W | Enumerated |  | {"0":"Off","1":"Auto","2":"On"} | {"0":"off","1":"auto","2":"on"} | TRUE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AUX_ON_Battery_Voltage | inverter_aux_on_battery_voltage | 42 | 42 | 41 | 1 | uint16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AUX_ON_Delay_Time | inverter_aux_on_delay_time | 43 | 43 | 42 | 1 | uint16 | R/W | Minutes | GSconfig_Time_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AUX_OFF_Battery_Voltage | inverter_aux_off_battery_voltage | 44 | 44 | 43 | 1 | uint16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AUX_OFF_Delay_Time | inverter_aux_off_delay_time | 45 | 45 | 44 | 1 | uint16 | R/W | Minutes | GSconfig_Time_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AUX_Relay_Mode | inverter_aux_relay_mode | 46 | 46 | 45 | 1 | uint16 | R/W | Enumerated |  | {"1":"Load Shed","2":"Gen Alert","3":"Fault","4":"Vent Fan","5":"Cool Fan","6":"DC Divert","7":"Grid Limit/IEEE","8":"AC Source Status","9":"AC Divert"} | {} | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AUX_Relay_Control | inverter_aux_relay_control | 47 | 47 | 46 | 1 | uint16 | R/W | Enumerated |  | {"0":"Off","1":"On","2":"Auto"} | {"0":"off","1":"on","2":"auto"} | TRUE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AUX_Relay_ON_Battery_Voltage | inverter_aux_relay_on_battery_voltage | 48 | 48 | 47 | 1 | uint16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AUX_Relay_ON_Delay_Time | inverter_aux_relay_on_delay_time | 49 | 49 | 48 | 1 | uint16 | R/W | Minutes | GSconfig_Time_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AUX_Relay_OFF_Battery_Voltage | inverter_aux_relay_off_battery_voltage | 50 | 50 | 49 | 1 | uint16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AUX_Relay_OFF_Delay_Time | inverter_aux_relay_off_delay_time | 51 | 51 | 50 | 1 | uint16 | R/W | Minutes | GSconfig_Time_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Stacking_Mode |  | 52 | 52 | 51 | 1 | uint16 | R | Enumerated |  | {"10":"Master","12":"Slave","17":"B Phase Master","18":"C Phase Master"} | {} | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Master_Power_Save_Level | inverter_master_power_save_level | 53 | 53 | 52 | 1 | uint16 | R/W |  |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Slave_Power_Save_Level | inverter_slave_power_save_level | 54 | 54 | 53 | 1 | uint16 | R/W |  |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Sell_Volts | inverter_sell_voltage | 55 | 55 | 54 | 1 | uint16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Grid_Tie_Window | inverter_grid_tie_window | 56 | 56 | 55 | 1 | uint16 | R/W | Enumerated |  | {"0":"IEEE","1":"User (GS8048 Only)"} | {} | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Grid_Tie_Enable | inverter_grid_tie_enable | 57 | 57 | 56 | 1 | uint16 | R/W | Enumerated |  | {"1":"Yes","0":"No"} | {} | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Grid_AC_Input_Voltage_Calibrate_Factor | inverter_grid_ac_input_voltage_calibrate_factor | 58 | 58 | 57 | 1 | int16 | R/W | Volts AC |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Gen_AC_Input_Voltage_Calibrate_Factor | inverter_gen_ac_input_voltage_calibrate_factor | 59 | 59 | 58 | 1 | int16 | R/W | Volts AC |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_AC_Output_Voltage_Calibrate_Factor | inverter_ac_output_voltage_calibrate_factor | 60 | 59 | 59 | 1 | int16 | R/W | Volts AC |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Battery_Voltage_Calibrate_Factor | inverter_battery_voltage_calibrate_factor | 61 | 60 | 60 | 1 | int16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_ReBulk_Volts | inverter_rebulk_voltage | 62 | 61 | 61 | 1 | uint16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Mini_Grid_LBX_Volts | inverter_mini_grid_lbx_voltage | 63 | 62 | 62 | 1 | uint16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Mini_Grid_LBX_Delay | inverter_mini_grid_lbx_delay | 64 | 63 | 63 | 1 | uint16 | R/W | Hours |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Grid_Zero_DoD_Volts | inverter_grid_zero_dod_voltage | 65 | 64 | 64 | 1 | uint16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Grid_Zero_DoD_Max_Offset_AC_Amps | inverter_grid_zero_dod_max_offset_ac_amps | 66 | 65 | 65 | 1 | uint16 | R/W | Amps | GSconfig_AC_Current_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Serial_Number |  | 67 | 75 | 66 | 9 | string (18) | R/W |  |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Model_Number |  | 76 | 84 | 75 | 9 | string (18) | R |  |  |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Module_Control | inverter_module_control | 85 | 85 | 84 | 1 | uint16 | R/W | Enumerated |  | {"0":"Auto","1":"Left","2":"Right","3":"Both"} | {} | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Model_Select | inverter_model_select | 86 | 86 | 85 | 1 | uint16 | R/W | Enumerated |  | {"0":"Dual Module","1":"Single Module"} | {} | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_Low_Battery_Cut_Out_Delay | inverter_low_battery_cut_out_delay | 87 | 87 | 86 | 1 | uint16 | R/W | Seconds | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_High_Battery_Cut_Out_Voltage | inverter_high_battery_cut_out_voltage | 88 | 88 | 87 | 1 | uint16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | GSconfig_High_Battery_Cut_In_Voltage | inverter_high_battery_cut_in_voltage | 89 | 89 | 88 | 1 | uint16 | R/W | DC Volts | GSconfig_DC_Voltage_SF |  |  | FALSE
64116 | inverter | Radian Inverter | Radian Inverter Configuration Block | 86 | Gsconfig_High_Battery_Cut_Out_Delay | inverter_gsconfig_high_battery_cut_out_delay | 90 | 90 | 89 | 1 | uint16 | R/W | Seconds | GSconfig_DC_Voltage_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_DID |  | 1 | 1 | 0 | 1 | uint16 | R |  |  |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Length |  | 2 | 2 | 1 | 1 | uint16 | R | Registers |  |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Port_number |  | 3 | 3 | 2 | 1 | uint16 | R |  |  |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_DC_Voltage_SF |  | 4 | 4 | 3 | 1 | int16 | R |  |  |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_AC_Current_SF |  | 5 | 5 | 4 | 1 | int16 | R |  |  |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_AC_Voltage_SF |  | 6 | 6 | 5 | 1 | int16 | R |  |  |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_AC_Frequency_SF |  | 7 | 7 | 6 | 1 | int16 | R |  |  |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Inverter_Output_Current |  | 8 | 8 | 7 | 1 | uint16 | R | Amps | GS_Single_AC_Current_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Inverter_Charge_Current |  | 9 | 9 | 8 | 1 | uint16 | R | Amps | GS_Single_AC_Current_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Inverter_Buy_Current |  | 10 | 10 | 9 | 1 | uint16 | R | Amps | GS_Single_AC_Current_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Inverter_Sell_Current |  | 11 | 11 | 10 | 1 | uint16 | R | Amps | GS_Single_AC_Current_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Grid_Input_AC_Voltage |  | 12 | 12 | 11 | 1 | uint16 | R | Volts AC | GS_Single_AC_Voltage_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Gen_Input_AC_Voltage |  | 13 | 13 | 12 | 1 | uint16 | R | Volts AC | GS_Single_AC_Voltage_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Output_AC_Voltage |  | 14 | 14 | 13 | 1 | uint16 | R | Volts AC | GS_Single_AC_Voltage_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Inverter_Operating_mode |  | 15 | 15 | 14 | 1 | uint16 | R | Enumerated |  | {"0":"Off","1":"Searching","2":"Inverting","3":"Charging","4":"Silent","5":"Float","6":"EQ","7":"Charger Off","8":"Support","9":"Selling","10":"Pass through","14":"Offsetting"} | {"0":"Off","1":"Searching","2":"Inverting","3":"Charging","4":"Silent","5":"Float","6":"Equalize","7":"Charger Off","8":"Support","9":"Sell","10":"Pass-through","11":"Slave Inverter On","12":"Slave Inverter Off","13":"Unknown","14":"Offsetting","15":"AGS Error","16":"Comm Error"} | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Error_Flags |  | 16 | 16 | 15 | 1 | uint16 | R | Bitfield |  | {"0x0001":"Low AC output voltage","0x0002":"Stacking error","0x0004":"Over temperature error","0x0008":"Low battery voltage","0x0010":"Phase loss","0x0020":"High battery voltage","0x0040":"AC output shorted","0x0080":"AC backfeed"} | {} | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Warning_Flags |  | 17 | 17 | 16 | 1 | uint16 | R | Bitfield |  | {"0x0001":"AC input frequency too high","0x0002":"AC input frequency too low","0x0004":"AC input voltage too low","0x0008":"AC input voltage too high","0x0010":"AC input current exceeds max","0x0020":"Temperature sensor bad","0x0040":"Communications error","0x0080":"Cooling fan fault"} | {} | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Battery_Voltage |  | 18 | 18 | 17 | 1 | uint16 | R | Volts DC | GS_Single_DC_Voltage_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Temp_Compensated_Target_Voltage |  | 19 | 19 | 18 | 1 | uint16 | R | Volts DC | GS_Single_DC_Voltage_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_AUX_Output_State |  | 20 | 20 | 19 | 1 | uint16 | R | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {} | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_AUX_Relay_Output_State |  | 21 | 21 | 20 | 1 | uint16 | R | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {"0":"disabled","1":"enabled"} | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_L_Module_Transformer_Temperature |  | 22 | 22 | 21 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_L_Module_Capacitor_Temperature |  | 23 | 23 | 22 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_L_Module_FET_Temperature |  | 24 | 24 | 23 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_R_Module_Transformer_Temperature |  | 25 | 25 | 24 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_R_Module_Capacitor_Temperature |  | 26 | 26 | 25 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_R_Module_FET_Temperature |  | 27 | 27 | 26 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Battery_Temperature |  | 28 | 28 | 27 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_AC_Input_Selection |  | 29 | 29 | 28 | 1 | uint16 | R | Enumerated |  | {"0":"Grid","1":"Gen"} | {} | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_AC_Input_Frequency |  | 30 | 30 | 29 | 1 | uint16 | R | Hz | GS_Single_AC_Frequency_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_AC_Input_Voltage |  | 31 | 31 | 30 | 1 | uint16 | R | Volts AC | GS_Single_AC_Voltage_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_AC_Input_State |  | 32 | 32 | 31 | 1 | uint16 | R | Enumerated |  | {"1":"AC Use","0":"AC_Drop"} | {"0":"AC Drop","1":"AC Use"} | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Minimum_AC_Input_Voltage |  | 33 | 33 | 32 | 1 | uint16 | R | Volts AC | GS_Single_AC_Voltage_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Maximum_AC_Input_Voltage |  | 34 | 34 | 33 | 1 | uint16 | R | Volts AC | GS_Single_AC_Voltage_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Sell_Status |  | 35 | 35 | 34 | 1 | uint16 | R | Bitfield |  | {"0x0001":"AC input frequency too high","0x0002":"AC input frequency too low","0x0004":"AC input voltage too low","0x0008":"AC input voltage too high","0x0010":"Awaiting sell delay","0x0020":"Sell disabled","0x0040":"Battery voltage less than target"} | {} | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_kWh_SF |  | 36 | 36 | 35 | 1 | int16 | R |  |  |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_AC1_Buy_kWh |  | 37 | 37 | 36 | 1 | uint16 | R | kWh | GS_Single_kWh_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_AC2_Buy_kWh |  | 38 | 38 | 37 | 1 | uint16 | R | kWh | GS_Single_kWh_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_AC1_Sell_kWh |  | 39 | 39 | 38 | 1 | uint16 | R | kWh | GS_Single_kWh_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_AC2_Sell_kWh |  | 40 | 40 | 39 | 1 | uint16 | R | kWh | GS_Single_kWh_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Output_kWh |  | 41 | 41 | 40 | 1 | uint16 | R | kWh | GS_Single_kWh_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Charger_kWh |  | 42 | 42 | 41 | 1 | uint16 | R | kWh | GS_Single_kWh_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Output_kW |  | 43 | 43 | 42 | 1 | uint16 | R | kW | GS_Single_kWh_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Buy_kW |  | 44 | 44 | 43 | 1 | uint16 | R | kW | GS_Single_kWh_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Sell_kW |  | 45 | 45 | 44 | 1 | uint16 | R | kW | GS_Single_kWh_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Charge_kW |  | 46 | 46 | 45 | 1 | uint16 | R | kW | GS_Single_kWh_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_Load_kW |  | 47 | 47 | 46 | 1 | uint16 | R | kW | GS_Single_kWh_SF |  |  | FALSE
64117 | inverter | Radian Single Phase Inverter | Single Phase Radian Inverter Real Time Block | 46 | GS_Single_AC_Couple_kW |  | 48 | 48 | 47 | 1 | uint16 | R | kW | GS_Single_kWh_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_DID |  | 1 | 1 | 0 | 1 | uint16 | R |  |  |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Length |  | 2 | 2 | 1 | 1 | uint16 | R | Registers |  |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Port_number |  | 3 | 3 | 2 | 1 | uint16 | R |  |  |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_DC_Voltage_SF |  | 4 | 4 | 3 | 1 | int16 | R |  |  |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_AC_Current_SF |  | 5 | 5 | 4 | 1 | int16 | R |  |  |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_AC_Voltage_SF |  | 6 | 6 | 5 | 1 | int16 | R |  |  |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_AC_Frequency_SF |  | 7 | 7 | 6 | 1 | int16 | R |  |  |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Inverter_Output_Current |  | 8 | 8 | 7 | 1 | uint16 | R | Amps | FX_AC_Current_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Inverter_Charge_Current |  | 9 | 9 | 8 | 1 | uint16 | R | Amps | FX_AC_Current_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Inverter_Buy_Current |  | 10 | 10 | 9 | 1 | uint16 | R | Amps | FX_AC_Current_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Inverter_Sell_Current |  | 11 | 11 | 10 | 1 | uint16 | R | Amps | FX_AC_Current_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Output_AC_Voltage |  | 12 | 12 | 11 | 1 | uint16 | R | Volts AC | FX_AC_Voltage_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Inverter_Operating_Mode |  | 13 | 13 | 12 | 1 | uint16 | R | Enumerated |  | {"0":"Off","1":"Searching","2":"Inverting","3":"Charging","4":"Silent","5":"Float","6":"EQ","7":"Charger Off","8":"Support","9":"Selling","10":"Pass through","14":"Offsetting"} | {"0":"Off","1":"Searching","2":"Inverting","3":"Charging","4":"Silent","5":"Float","6":"Equalize","7":"Charger Off","8":"Support","9":"Sell","10":"Pass-through","11":"Slave Inverter On","12":"Slave Inverter Off","13":"Unknown","14":"Offsetting","15":"AGS Error","16":"Comm Error"} | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Error_Flags |  | 14 | 14 | 13 | 1 | uint16 | R | Bitfield |  | {"0x0001":"Low AC output voltage","0x0002":"Stacking error","0x0004":"Over temperature error","0x0008":"Low battery voltage","0x0010":"Phase loss","0x0020":"High battery voltage","0x0040":"AC output shorted","0x0080":"AC backfeed"} | {} | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Warning_Flags |  | 15 | 15 | 14 | 1 | uint16 | R | Bitfield |  | {"0x0001":"AC input frequency too high","0x0002":"AC input frequency too low","0x0004":"AC input voltage too low","0x0008":"AC input voltage too high","0x0010":"AC input current exceeds max","0x0020":"Temperature sensor bad","0x0040":"Communications error","0x0080":"Cooling fan fault"} | {} | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Battery_Voltage |  | 16 | 16 | 15 | 1 | uint16 | R | Volts DC | FX_DC_Voltage_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Temp_Compensated_Target_Voltage |  | 17 | 17 | 16 | 1 | uint16 | R | Volts DC | FX_DC_Voltage_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_AUX_Output_State |  | 18 | 18 | 17 | 1 | uint16 | R | Enumerated |  | {"0":"Disabled","1":"Enabled"} | {"0":"disabled","1":"enabled"} | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Transformer_Temperature |  | 19 | 19 | 18 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Capacitor_Temperature |  | 20 | 20 | 19 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_FET_Temperature |  | 21 | 21 | 20 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_AC_Input_Frequency |  | 22 | 22 | 21 | 1 | uint16 | R | Hz | FX_AC_Frequency_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_AC_Input_Voltage |  | 23 | 23 | 22 | 1 | uint16 | R | Volts AC | FX_AC_Voltage_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_AC_Input_State |  | 24 | 24 | 23 | 1 | uint16 | R | Enumerated |  | {"1":"AC Use","0":"AC_Drop"} | {"0":"AC Drop","1":"AC Use"} | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Minimum_AC_Input_Voltage |  | 25 | 25 | 24 | 1 | uint16 | R | Volts AC | FX_AC_Voltage_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Maximum_AC_Input_Voltage |  | 26 | 26 | 25 | 1 | uint16 | R | Volts AC | FX_AC_Voltage_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Sell_Status |  | 27 | 27 | 26 | 1 | uint16 | R | Bitfield |  | {"0x0001":"AC input frequency too high","0x0002":"AC input frequency too low","0x0004":"AC input voltage too low","0x0008":"AC input voltage too high","0x0010":"Awaiting sell delay","0x0020":"Sell disabled","0x0040":"Battery voltage less than target","0x0080":"AC2 selected"} | {} | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_kWh_SF |  | 28 | 28 | 27 | 1 | int16 | R |  |  |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Buy_kWh |  | 29 | 29 | 28 | 1 | uint16 | R | kWh | FX_kWh_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Sell_kWh |  | 30 | 30 | 29 | 1 | uint16 | R | kWh | FX_kWh_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Output_kWh |  | 31 | 31 | 30 | 1 | uint16 | R | kWh | FX_kWh_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Charger_kWh |  | 32 | 32 | 31 | 1 | uint16 | R | kWh | FX_kWh_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Output_kW |  | 33 | 33 | 32 | 1 | uint16 | R | kWh | FX_kWh_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Buy_kW |  | 34 | 34 | 33 | 1 | uint16 | R | kWh | FX_kWh_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Sell_kW |  | 35 | 35 | 34 | 1 | uint16 | R | kWh | FX_kWh_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Charge_kW |  | 36 | 36 | 35 | 1 | uint16 | R | kWh | FX_kWh_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_Load_kW |  | 37 | 37 | 36 | 1 | uint16 | R | kWh | FX_kWh_SF |  |  | FALSE
64113 | inverter | FX Inverter | FX Inverter Real Time Block | 32 | FX_AC_Couple_kW |  | 38 | 38 | 37 | 1 | uint16 | R | kWh | FX_kWh_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_DID |  | 1 | 1 | 0 | 1 | uint16 | R |  |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Length |  | 2 | 2 | 1 | 1 | uint16 | R | Registers |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Port_Number |  | 3 | 3 | 2 | 1 | uint16 | R |  |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_DC_Voltage_SF |  | 4 | 4 | 3 | 1 | int16 | R |  |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AC_Current_SF |  | 5 | 5 | 4 | 1 | int16 | R |  |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AC_Voltage_SF |  | 6 | 6 | 5 | 1 | int16 | R |  |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Time_SF |  | 7 | 7 | 6 | 1 | int16 | R |  |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Major_Firmware_Number |  | 8 | 8 | 7 | 1 | uint16 | R |  |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Mid_Firmware_Number |  | 9 | 9 | 8 | 1 | uint16 | R |  |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Minor_Firmware_Number |  | 10 | 10 | 9 | 1 | uint16 | R |  |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Absorb_Volts | inverter_absorb_voltage | 11 | 11 | 10 | 1 | uint16 | R/W | DC Volts | FXconfig_DC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Absorb_Time_Hours | inverter_absorb_time_hours | 12 | 12 | 11 | 1 | uint16 | R/W | Hours | FXconfig_Time_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Float_Volts | inverter_float_voltage | 13 | 13 | 12 | 1 | uint16 | R/W | DC Volts | FXconfig_DC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Float_Time_Hours | inverter_float_time_hours | 14 | 14 | 13 | 1 | uint16 | R/W | Hours | FXconfig_Time_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_ReFloat_Volts | inverter_refloat_voltage | 15 | 15 | 14 | 1 | uint16 | R/W | DC Volts | FXconfig_DC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_EQ_Volts | inverter_eq_voltage | 16 | 16 | 15 | 1 | uint16 | R/W | DC Volts | FXconfig_DC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_EQ_Time_Hours | inverter_eq_time_hours | 17 | 17 | 16 | 1 | uint16 | R/W | Hours | FXconfig_Time_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Search_Sensitivity | inverter_search_sensitivity | 18 | 18 | 17 | 1 | uint16 | R/W |  |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Search_Pulse_Length | inverter_search_pulse_length | 19 | 19 | 18 | 1 | uint16 | R/W | Cycles |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Search_Pulse_Spacing | inverter_search_pulse_spacing | 20 | 20 | 19 | 1 | uint16 | R/W | Cycles |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AC_Input_Type | inverter_ac_input_type | 21 | 21 | 20 | 1 | uint16 | R/W | Enumerated |  | {"0":"Grid","1":"Gen","2":"Grid Zero"} | {"0":"GridTied","1":"Generator","2":"GridZero"} | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | Fxconfig_Input_Support | inverter_fxconfig_input_support | 22 | 22 | 21 | 1 | uint16 | R/W | Enumerated |  | {"1":"Yes","0":"No (only validif AC Input Type is Gen)"} | {} | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Grid_AC_Input_Current_Limit | inverter_grid_ac_input_current_limit | 23 | 23 | 22 | 1 | uint16 | R/W | Amps | FXconfig_AC_Current_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Gen_AC_Input_Current_Limit | inverter_gen_ac_input_current_limit | 24 | 24 | 23 | 1 | uint16 | R/W | Amps | FXconfig_AC_Current_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Charger_AC_Input_Current_Limit | inverter_charger_ac_input_current_limit | 25 | 25 | 24 | 1 | uint16 | R/W | Amps | FXconfig_AC_Current_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Charger_Operating_Mode | inverter_charger_operating_mode | 26 | 26 | 25 | 1 | uint16 | R/W | Enumerated |  | {"0":"Charger Off","1":"Charger Auto","2":"Charger On"} | {"0":"Off","1":"Auto","2":"On"} | TRUE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Grid_Lower_Input_Voltage_Limit | inverter_grid_lower_input_voltage_limit | 27 | 27 | 26 | 1 | uint16 | R/W | Volts AC | FXconfig_AC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Grid_Upper_Input_Voltage_Limit | inverter_grid_upper_input_voltage_limit | 28 | 28 | 27 | 1 | uint16 | R/W | Volts AC | FXconfig_AC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Grid_Transfer_Delay | inverter_grid_transfer_delay | 29 | 29 | 28 | 1 | uint16 | R/W | Minutes |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Gen_Lower_Input_Voltage_Limit | inverter_gen_lower_input_voltage_limit | 30 | 30 | 29 | 1 | uint16 | R/W | Volts AC | FXconfig_AC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Gen_Upper_Input_Voltage_Limit | inverter_gen_upper_input_voltage_limit | 31 | 31 | 30 | 1 | uint16 | R/W | Volts AC | FXconfig_AC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Gen_Transfer_Delay | inverter_gen_transfer_delay | 32 | 32 | 31 | 1 | uint16 | R/W | Cycles |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Gen_Connect_Delay | inverter_gen_connect_delay | 33 | 33 | 32 | 1 | uint16 | R/W | Minutes | FXconfig_Time_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AC_Output_Voltage | inverter_ac_output_voltage | 34 | 34 | 33 | 1 | uint16 | R/W | Volts AC | FXconfig_AC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Low_Battery_Cut_Out_Voltage | inverter_low_battery_cut_out_voltage | 35 | 35 | 34 | 1 | uint16 | R/W | DC Volts | FXconfig_DC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Low_Battery_Cut_In_Voltage | inverter_low_battery_cut_in_voltage | 36 | 36 | 35 | 1 | uint16 | R/W | DC Volts | FXconfig_DC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AUX_Mode | inverter_aux_mode | 37 | 37 | 36 | 1 | uint16 | R/W | Enumerated |  | {"0":"Remote","1":"Load Shed","2":"Gen Alert","3":"Fault","4":"Vent Fan","5":"Cool Fan","6":"Divert DC","7":"Divert AC","8":"AC Drop"} | {} | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AUX_Control | inverter_aux_control | 38 | 38 | 37 | 1 | uint16 | R/W | Enumerated |  | {"0":"Off","1":"Auto","2":"On"} | {"0":"off","1":"auto","2":"on"} | TRUE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AUX_Load_Shed_Enable_Voltage | inverter_aux_load_shed_enable_voltage | 39 | 39 | 38 | 1 | uint16 | R/W | DC Volts | FXconfig_DC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AUX_Gen_Alert_On_Voltage | inverter_aux_gen_alert_on_voltage | 40 | 40 | 39 | 1 | uint16 | R/W | DC Volts | FXconfig_DC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AUX_Gen_Alert_On_Delay | inverter_aux_gen_alert_on_delay | 41 | 41 | 40 | 1 | uint16 | R/W | Minutes |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AUX_Gen_Alert_Off_Voltage | inverter_aux_gen_alert_off_voltage | 42 | 42 | 41 | 1 | uint16 | R/W | DC Volts | FXconfig_DC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AUX_Gen_Alert_Off_Delay | inverter_aux_gen_alert_off_delay | 43 | 43 | 42 | 1 | uint16 | R/W | Minutes |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AUX_Vent_Fan_Enable_Voltage | inverter_aux_vent_fan_enable_voltage | 44 | 44 | 43 | 1 | uint16 | R/W | DC Volts | FXconfig_DC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AUX_Vent_Fan_Off_Period | inverter_aux_vent_fan_off_period | 45 | 45 | 44 | 1 | uint16 | R/W | Minutes |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AUX_Divert_Enable_Voltage | inverter_aux_divert_enable_voltage | 46 | 46 | 45 | 1 | uint16 | R/W | DC Volts | FXconfig_DC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AUX_Divert_Off_Delay | inverter_aux_divert_off_delay | 47 | 47 | 46 | 1 | uint16 | R/W | Minutes |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Stacking_Mode |  | 48 | 48 | 47 | 1 | uint16 | R | Enumerated |  | {"0":"1-2phase Master","1":"Classic Slave","2":"OB Slave L1","3":"OB Slave L2","4":"3phase Master","5":"3phase Slave","10":"Master","11":"Classic Slave","12":"OB Slave L1","13":"OB Slave L2","14":"3phase OB Slave A","15":"3phase OB Slave B","16":"3phase OB Slave C","17":"3phase Classic B","18":"3phase Classic C","19":"Independent"} | {} | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Master_Power_Save_Level | inverter_master_power_save_level | 49 | 49 | 48 | 1 | uint16 | R/W |  |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Slave_Power_Save_Level | inverter_slave_power_save_level | 50 | 50 | 49 | 1 | uint16 | R/W |  |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Sell_Volts | inverter_sell_voltage | 51 | 51 | 50 | 1 | uint16 | R/W | DC Volts | FXconfig_DC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Grid_Tie_Window | inverter_grid_tie_window | 52 | 52 | 51 | 1 | uint16 | R/W | Enumerated |  | {"0":"IEEE","1":"User"} | {} | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Grid_Tie_Enable | inverter_grid_tie_enable | 53 | 53 | 52 | 1 | uint16 | R/W | Enumerated |  | {"1":"Yes","0":"No"} | {} | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AC_Input_Voltage_Calibrate_Factor | inverter_ac_input_voltage_calibrate_factor | 54 | 54 | 53 | 1 | int16 | R/W | Volts AC |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_AC_Output_Voltage_Calibrate_Factor | inverter_ac_output_voltage_calibrate_factor | 55 | 55 | 54 | 1 | int16 | R/W | Volts AC |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Battery_Voltage_Calibrate_Factor | inverter_battery_voltage_calibrate_factor | 56 | 56 | 55 | 1 | int16 | R/W | DC Volts | FXconfig_DC_Voltage_SF |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Serial_Number |  | 57 | 65 | 56 | 9 | string (18) | R |  |  |  |  | FALSE
64114 | inverter | FX Inverter | FX Inverter Configuration Block | 72 | FXconfig_Model_Number |  | 66 | 74 | 65 | 9 | string (18) | R |  |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_DID |  | 1 | 1 | 0 | 1 | uint16 | R |  |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Length |  | 2 | 2 | 1 | 1 | uint16 | R | Registers |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Port_Number |  | 3 | 3 | 2 | 1 | uint16 | R |  |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_DC_Voltage_SF |  | 4 | 4 | 3 | 1 | int16 | R |  |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_DC_Current_SF |  | 5 | 5 | 4 | 1 | int16 | R |  |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_kWh_SF |  | 6 | 6 | 5 | 1 | int16 | R |  |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Major_Firmware_Number |  | 7 | 7 | 6 | 1 | uint16 | R |  |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Mid_Firmware_Number |  | 8 | 8 | 7 | 1 | uint16 | R |  |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Minor_Firmware_Number |  | 9 | 9 | 8 | 1 | uint16 | R |  |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Battery_Capacity | battery_monitor_battery_capacity | 10 | 10 | 9 | 1 | uint16 | R/W | AH |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Charged_Volts | battery_monitor_charged_voltage | 11 | 11 | 10 | 1 | uint16 | R/W | DC Volts | FNconfig_DC_Voltage_SF |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Charged_Time | battery_monitor_charged_time | 12 | 12 | 11 | 1 | uint16 | R/W | Minutes |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Battery_Charged_Amps | battery_monitor_battery_charged_amps | 13 | 13 | 12 | 1 | uint16 | R/W | Amps | FNconfig_DC_Current_SF |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Charge_Factor | battery_monitor_charge_factor | 14 | 14 | 13 | 1 | uint16 | R/W | Percent |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Shunt_A_Enabled | battery_monitor_shunt_a_enabled | 15 | 15 | 14 | 1 | uint16 | R/W | Enumerated |  | {"0":"Enabled","1":"Disabled"} | {"0":"ON","1":"OFF"} | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Shunt_B_Enabled | battery_monitor_shunt_b_enabled | 16 | 16 | 15 | 1 | uint16 | R/W | Enumerated |  | {"0":"Enabled","1":"Disabled"} | {"0":"ON","1":"OFF"} | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Shunt_C_Enabled | battery_monitor_shunt_c_enabled | 17 | 17 | 16 | 1 | uint16 | R/W | Enumerated |  | {"0":"Enabled","1":"Disabled"} | {"0":"ON","1":"OFF"} | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Relay_Control | battery_monitor_relay_control | 18 | 18 | 17 | 1 | uint16 | R/W | Enumerated |  | {"0":"Off","1":"Auto","2":"On"} | {"0":"off","1":"auto","2":"on"} | TRUE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Relay_Invert_Logic | battery_monitor_relay_invert_logic | 19 | 19 | 18 | 1 | uint16 | R/W | Enumerated |  | {"0":"Invert Logic","1":"Normal"} | {} | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Relay_High_Voltage | battery_monitor_relay_high_voltage | 20 | 20 | 19 | 1 | uint16 | R/W | DC Volts | FNconfig_DC_Voltage_SF |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Relay_Low_Voltage | battery_monitor_relay_low_voltage | 21 | 21 | 20 | 1 | uint16 | R/W | DC Volts | FNconfig_DC_Voltage_SF |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Relay_SOC_High | battery_monitor_relay_soc_high | 22 | 22 | 21 | 1 | uint16 | R/W | Percent |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Relay_SOC_Low | battery_monitor_relay_soc_low | 23 | 23 | 22 | 1 | uint16 | R/W | Percent |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Relay_High_Enable_Delay | battery_monitor_relay_high_enable_delay | 24 | 24 | 23 | 1 | uint16 | R/W | Minutes |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Relay_Low_Enable_Delay | battery_monitor_relay_low_enable_delay | 25 | 25 | 24 | 1 | uint16 | R/W | Minutes |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Set_Data_Log_Day_Offset | battery_monitor_data_log_day_offset | 26 | 26 | 25 | 1 | uint16 | R/W | Days |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Get_Current_Data_Log_Day_Offset |  | 27 | 27 | 26 | 1 | uint16 | R | Days |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Datalog_Minimum_SOC |  | 28 | 28 | 27 | 1 | uint16 | R | Percent |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Datalog_Input_AH |  | 29 | 29 | 28 | 1 | uint16 | R | AH |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Datalog_Input_kWh |  | 30 | 30 | 29 | 1 | uint16 | R | kWh | FNconfig_kWh_SF |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Datalog_Output_AH |  | 31 | 31 | 30 | 1 | uint16 | R | AH |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Datalog_Output_kWh |  | 32 | 32 | 31 | 1 | uint16 | R | kWh | FNconfig_kWh_SF |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Datalog_NET_AH |  | 33 | 33 | 32 | 1 | uint16 | R | AH |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Datalog_NET_kWh |  | 34 | 34 | 33 | 1 | uint16 | R | kWh | FNconfig_kWh_SF |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Clear_Data_Log_Read |  | 35 | 35 | 34 | 1 | uint16 | R |  |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Clear_Data_Log_Write_Complement |  | 36 | 36 | 35 | 1 | uint16 | W |  |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Serial_Number |  | 37 | 45 | 36 | 9 | string (18) | R |  |  |  |  | FALSE
64119 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Configuration Block | 52 | FNconfig_Model_Number |  | 46 | 54 | 45 | 9 | string (18) | R |  |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_DID |  | 1 | 1 | 0 | 1 | uint16 | R |  |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Length |  | 2 | 2 | 1 | 1 | uint16 | R | Registers |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Port_Number |  | 3 | 3 | 2 | 1 | uint16 | R |  |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_DC_Voltage_SF |  | 4 | 4 | 3 | 1 | int16 | R |  |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_DC_Current_SF |  | 5 | 5 | 4 | 1 | int16 | R |  |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Time_SF |  | 6 | 6 | 5 | 1 | int16 | R |  |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_kWh_SF |  | 7 | 7 | 6 | 1 | int16 | R |  |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_kW_SF |  | 8 | 8 | 7 | 1 | int16 | R |  |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_A_Current |  | 9 | 9 | 8 | 1 | int16 | R | Amps | FN_DC_Current_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_B_Current |  | 10 | 10 | 9 | 1 | int16 | R | Amps | FN_DC_Current_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_C_Current |  | 11 | 11 | 10 | 1 | int16 | R | Amps | FN_DC_Current_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Battery_Voltage |  | 12 | 12 | 11 | 1 | uint16 | R | Volts | FN_DC_Voltage_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Battery_Current |  | 13 | 13 | 12 | 1 | int16 | R | Amps | FN_DC_Current_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Battery_Temperature |  | 14 | 14 | 13 | 1 | int16 | R | Degrees C |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Status_Flags |  | 15 | 15 | 14 | 1 | uint16 | R | Bitfield |  | {"0x0001":"AUX relay enabled","0x0002":"Charge parameters met"} | {} | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_A_Accumulated_AH |  | 16 | 16 | 15 | 1 | int16 | R | AH |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_A_Accumulated_kWh |  | 17 | 17 | 16 | 1 | int16 | R | kWh | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_B_Accumulated_AH |  | 18 | 18 | 17 | 1 | int16 | R | AH |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_B_Accumulated_kWh |  | 19 | 19 | 18 | 1 | int16 | R | kWh | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_C_Accumulated_AH |  | 20 | 20 | 19 | 1 | int16 | R | AH |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_C_Accumulated_kWh |  | 21 | 21 | 20 | 1 | int16 | R | kWh | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Input_Current |  | 22 | 22 | 21 | 1 | uint16 | R | Amps | FN_DC_Current_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Output_Current |  | 23 | 23 | 22 | 1 | uint16 | R | Amps | FN_DC_Current_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Input_kW |  | 24 | 24 | 23 | 1 | uint16 | R | kW | FN_kW_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Output_kW |  | 25 | 25 | 24 | 1 | uint16 | R | kW | FN_kW_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Net_kW |  | 26 | 26 | 25 | 1 | int16 | R | kW | FN_kW_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Days_Since_Charge_Parameters_Met |  | 27 | 27 | 26 | 1 | uint16 | R | Days | FN_Time_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_State_Of_Charge |  | 28 | 28 | 27 | 1 | uint16 | R | Percent |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Todays_Minimum_SOC |  | 29 | 29 | 28 | 1 | uint16 | R | Percent |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Todays_Maximum_SOC |  | 30 | 30 | 29 | 1 | uint16 | R | Percent |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Todays_NET_Input_AH |  | 31 | 31 | 30 | 1 | uint16 | R | AH |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Todays_NET_Input_kWh |  | 32 | 32 | 31 | 1 | uint16 | R | kWh | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Todays_NET_Output_AH |  | 33 | 33 | 32 | 1 | uint16 | R | AH |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Todays_NET_Output_kWh |  | 34 | 34 | 33 | 1 | uint16 | R | kWh | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Todays_NET_Battery_AH |  | 35 | 35 | 34 | 1 | int16 | R | AH |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Todays_NET_Battery_kWh |  | 36 | 36 | 35 | 1 | int16 | R | kWh | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Charge_Factor_Corrected_NET_Battery_AH |  | 37 | 37 | 36 | 1 | int16 | R | AH |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Charge_Factor_Corrected_NET_Battery_kWh |  | 38 | 38 | 37 | 1 | int16 | R | kWh | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Todays_Minimum_Battery_Voltage |  | 39 | 39 | 38 | 1 | uint16 | R | Volts | FN_DC_Voltage_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Todays_Minimum_Battery_Time |  | 40 | 41 | 39 | 2 | uint32 | R | Seconds |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Todays_Maximum_Battery_Voltage |  | 42 | 42 | 41 | 1 | uint16 | R | Volts | FN_DC_Voltage_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Todays_Maximum_Battery_Time |  | 43 | 44 | 42 | 2 | uint32 | R | Seconds |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Cycle_Charge_Factor |  | 45 | 45 | 44 | 1 | uint16 | R | Percent |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Cycle_kWh_Charge_Efficiency |  | 46 | 46 | 45 | 1 | uint16 | R | Percent |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Total_Days_At_100_Percent |  | 47 | 47 | 46 | 1 | uint16 | R | Days | FN_Time_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Lifetime_kAH_Removed |  | 48 | 48 | 47 | 1 | uint16 | R | AH |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_A_Historical_Returned_To_Battery_AH |  | 49 | 49 | 48 | 1 | uint16 | R | AH |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_A_Historical_Returned_To_Battery_kWh |  | 50 | 50 | 49 | 1 | uint16 | R | kWh | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_A_Historical_Removed_From_Battery_AH |  | 51 | 51 | 50 | 1 | uint16 | R | AH |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_A_Historical_Removed_From_Battery_kWh |  | 52 | 52 | 51 | 1 | uint16 | R | kWh | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_A_Maximum_Charge_Rate |  | 53 | 53 | 52 | 1 | uint16 | R | Amps | FN_DC_Current_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_A_Maximum_Charge_Rate_kW |  | 54 | 54 | 53 | 1 | uint16 | R | kW | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_A_Maximum_Discharge_Rate |  | 55 | 55 | 54 | 1 | int16 | R | Amps | FN_DC_Current_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_A_Maximum_Discharge_Rate_kW |  | 56 | 56 | 55 | 1 | int16 | R | kW | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_B_Historical_Returned_To_Battery_AH |  | 57 | 57 | 56 | 1 | uint16 | R | AH |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_B_Historical_Returned_To_Battery_kWh |  | 58 | 58 | 57 | 1 | uint16 | R | kWh | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_B_Historical_Removed_From_Battery_AH |  | 59 | 59 | 58 | 1 | uint16 | R | AH |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_B_Historical_Removed_From_Battery_kWh |  | 60 | 60 | 59 | 1 | uint16 | R | kWh | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_B_Maximum_Charge_Rate |  | 61 | 61 | 60 | 1 | uint16 | R | Amps | FN_DC_Current_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_B_Maximum_Charge_Rate_kW |  | 62 | 62 | 61 | 1 | uint16 | R | kW | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_B_Maximum_Discharge_Rate |  | 63 | 63 | 62 | 1 | int16 | R | Amps | FN_DC_Current_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_B_Maximum_Discharge_Rate_kW |  | 64 | 64 | 63 | 1 | int16 | R | kW | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_C_Historical_Returned_To_Battery_AH |  | 65 | 65 | 64 | 1 | uint16 | R | AH |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_C_Historical_Returned_To_Battery_kWh |  | 66 | 66 | 65 | 1 | uint16 | R | kWh | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_C_Historical_Removed_From_Battery_AH |  | 67 | 67 | 66 | 1 | uint16 | R | AH |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_C_Historical_Removed_From_Battery_kWh |  | 68 | 68 | 67 | 1 | uint16 | R | kWh | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_C_Maximum_Charge_Rate |  | 69 | 69 | 68 | 1 | uint16 | R | Amps | FN_DC_Current_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_C_Maximum_Charge_Rate_kW |  | 70 | 70 | 69 | 1 | uint16 | R | kW | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_C_Maximum_Discharge_Rate |  | 71 | 71 | 70 | 1 | int16 | R | Amps | FN_DC_Current_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_C_Maximum_Discharge_Rate_kW |  | 72 | 72 | 71 | 1 | int16 | R | kW | FN_kWh_SF |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_A_Reset_Maximum_Data |  | 73 | 73 | 72 | 1 | uint16 | R |  |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_A_Reset_Maximum_Data_Write_Complement |  | 74 | 74 | 73 | 1 | uint16 | W |  |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_B_Reset_Maximum_Data |  | 75 | 75 | 74 | 1 | uint16 | R |  |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_B_Reset_Maximum_Data_Write_Complement |  | 76 | 76 | 75 | 1 | uint16 | W |  |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_C_Reset_Maximum_Data |  | 77 | 77 | 76 | 1 | uint16 | R |  |  |  |  | FALSE
64118 | battery_monitor | FLEXnet-DC Battery Monitor | FLEXnet-DC Real Time Block | 76 | FN_Shunt_C_Reset_Maximum_Data_Write_Complement |  | 78 | 78 | 77 | 1 | uint16 | W |  |  |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_DID |  | 1 | 1 | 0 | 1 | uint16 | R |  |  |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Length |  | 2 | 2 | 1 | 1 | uint16 | R | Registers |  |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_DC_Voltage_SF |  | 3 | 3 | 2 | 1 | int16 | R |  |  |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_AC_Current_SF |  | 4 | 4 | 3 | 1 | int16 | R |  |  |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Time_SF |  | 5 | 5 | 4 | 1 | int16 | R |  |  |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Bulk_Charge_Enable_Disable | system_bulk_charge_enable_disable | 6 | 6 | 5 | 1 | uint16 | W | Enumerated |  | {"1":"Start Bulk","2":"Stop Bulk","3":"Start EQ Charge","4":"Stop EQ Charge"} | {"1":"StartBulk","2":"StopBulk","3":"StartEQ","4":"StopEQ"} | TRUE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Inverter_AC_Drop_Use | system_inverter_ac_drop_use | 7 | 7 | 6 | 1 | uint16 | W | Enumerated |  | {"1":"Use","2":"Drop"} | {} | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Set_Inverter_Mode | system_inverter_mode | 8 | 8 | 7 | 1 | uint16 | W | Enumerated |  | {"1":"Off","2":"Search","3":"On"} | {"1":"off","2":"search","3":"on"} | TRUE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Grid_Tie_Mode | system_grid_tie_mode | 9 | 9 | 8 | 1 | uint16 | W | Enumerated |  | {"1":"Enable","2":"Disable"} | {} | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Set_Inverter_Charger_Mode | system_inverter_charger_mode | 10 | 10 | 9 | 1 | uint16 | W | Enumerated |  | {"1":"Off","2":"Auto","3":"On"} | {} | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Control_Status |  | 11 | 11 | 10 | 1 | uint16 | R | Bitfield |  | {"0x0001":"Bulk Charging","0x0002":"Float Charging","0x0004":"Inverter AC Input Use","0x0008":"Inverter Off","0x0010":"Inverter Search Mode","0x0020":"Inverter On","0x0040":"Inverter Grid-Tie Enabled","0x0080":"Inverter Charger Disabled","0x0100":"Inverter Charger Auto Mode","0x0200":"Inverter Charger Bulk and Float Mode","0x0400":"EQ Charging"} | {} | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Set_Sell_Voltage | system_sell_voltage | 12 | 12 | 11 | 1 | uint16 | R/W | Volts | OB_DC_Voltage_SF |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Set_Radian_Inverter_Sell_Current_Limit | system_radian_inverter_sell_current_limit | 13 | 13 | 12 | 1 | uint16 | R/W | Amps | OB_AC_Current_SF |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Set_Absorb_Voltage | system_absorb_voltage | 14 | 14 | 13 | 1 | uint16 | R/W | Volts | OB_DC_Voltage_SF |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Set_Absorb_Time | system_absorb_time | 15 | 15 | 14 | 1 | uint16 | R/W | Hours | OB_Time_SF |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Set_Float_Voltage | system_float_voltage | 16 | 16 | 15 | 1 | uint16 | R/W | Volts | OB_DC_Voltage_SF |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Set_Float_Time | system_float_time | 17 | 17 | 16 | 1 | uint16 | R/W | Hours | OB_Time_SF |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Set_Inverter_Charger_Current_Limit | system_inverter_charger_current_limit | 18 | 18 | 17 | 1 | uint16 | R/W | Amps | OB_AC_Current_SF |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Set_Inverter_AC1_Current_Limit | system_inverter_ac1_current_limit | 19 | 19 | 18 | 1 | uint16 | R/W | Amps | OB_AC_Current_SF |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Set_Inverter_AC2_Current_Limit | system_inverter_ac2_current_limit | 20 | 20 | 19 | 1 | uint16 | R/W | Amps | OB_AC_Current_SF |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Set_AGS_OP_Mode | system_ags_op_mode | 21 | 21 | 20 | 1 | uint16 | R/W | Enumerated |  | {"0":"Off","1":"On","2":"Auto"} | {} | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_AGS_Operational_State |  | 22 | 22 | 21 | 1 | uint16 | R | Enumerated |  | {"0":"GEN_STOP","1":"GEN_STARTING","2":"GEN_RUNNING","3":"GEN_WARMUP","4":"GEN_COOLDOWN","5":"GEN_AWAITING_AC"} | {} | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_AGS_Operational_State_Timer |  | 23 | 23 | 22 | 1 | uint16 | R | Seconds |  |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Gen_Last_Run_Start_Time_GMT |  | 24 | 25 | 23 | 2 | uint32 | R | Seconds |  |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Gen_Last_Start_Run_Duration |  | 26 | 27 | 25 | 2 | uint32 | R | Seconds |  |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Set_AC_Output_Freq_Offline_Mode | system_ac_output_freq_offline_mode | 28 | 28 | 27 | 1 | uint16 | R/W | NA |  |  |  | FALSE
64120 | system | OutBack System | OutBack System Control Block | 27 | OB_Set_AC_Output_Offline_Freq | system_ac_output_offline_freq | 29 | 29 | 28 | 1 | uint16 | R/W | Hz | OB_DC_Voltage_SF |  |  | FALSE

## tables
table_name | key | value
OutBack_Error_Table | 0x0001 | High limit last write
OutBack_Error_Table | 0x0002 | Low limit last write
OutBack_Error_Table | 0x0004 | Last write invalid
OutBack_Error_Table | 0x0008 | DHCP failed
OutBack_Error_Table | 0x0010 | DNS resolve failure
OutBack_Error_Table | 0x0020 | SMTP authorization failed
OutBack_Error_Table | 0x0040 | SMTP send failed
OutBack_Error_Table | 0x0080 | FTP Error
OutBack_Error_Table | 0x0100 | SD-Card Error
OutBack_Error_Table | 0x0200 | SNTP failure
OutBack_Error_Table | 0x0400 | Write while locked
OutBack_Error_Table | 0x0800 | Device firmware updating not supported
OutBack_Error_Table | 0x1000 | Device firmware update file not found
OutBack_Error_Table | 0x2000 | Device firmware update file invalid
OutBack_Error_Table | 0x4000 | Device firmware update failure
OutBack_Status_Table | 0x0001 | Firmware update complete
Device_FW_Update_Register | 0xPPXX | ["XX = device port number to update: 0-10", "PP = FW Update percent complete 0-100%"]
GS_Error_Table | 0x0001 | Low AC output voltage
GS_Error_Table | 0x0002 | Stacking error
GS_Error_Table | 0x0004 | Over temperature error
GS_Error_Table | 0x0008 | Low battery voltage
GS_Error_Table | 0x0010 | Phase loss
GS_Error_Table | 0x0020 | High battery voltage
GS_Error_Table | 0x0040 | AC output shorted
GS_Error_Table | 0x0080 | AC backfeed
GS_Warning_Table | 0x0001 | AC input frequency too high
GS_Warning_Table | 0x0002 | AC input frequency too low
GS_Warning_Table | 0x0004 | AC input voltage too low
GS_Warning_Table | 0x0008 | AC input voltage too high
GS_Warning_Table | 0x0010 | AC input current exceeds max
GS_Warning_Table | 0x0020 | Temperature sensor bad
GS_Warning_Table | 0x0040 | Communications error
GS_Warning_Table | 0x0080 | Cooling fan fault
GS_Sell_Status_Table | 0x0001 | AC input frequency too high
GS_Sell_Status_Table | 0x0002 | AC input frequency too low
GS_Sell_Status_Table | 0x0004 | AC input voltage too low
GS_Sell_Status_Table | 0x0008 | AC input voltage too high
GS_Sell_Status_Table | 0x0010 | Awaiting sell delay
GS_Sell_Status_Table | 0x0020 | Sell disabled
GS_Sell_Status_Table | 0x0040 | Battery voltage less than target
FX_Error_Table | 0x0001 | Low AC output voltage
FX_Error_Table | 0x0002 | Stacking error
FX_Error_Table | 0x0004 | Over temperature error
FX_Error_Table | 0x0008 | Low battery voltage
FX_Error_Table | 0x0010 | Phase loss
FX_Error_Table | 0x0020 | High battery voltage
FX_Error_Table | 0x0040 | AC output shorted
FX_Error_Table | 0x0080 | AC backfeed
FX_Warning_Table | 0x0001 | AC input frequency too high
FX_Warning_Table | 0x0002 | AC input frequency too low
FX_Warning_Table | 0x0004 | AC input voltage too low
FX_Warning_Table | 0x0008 | AC input voltage too high
FX_Warning_Table | 0x0010 | AC input current exceeds max
FX_Warning_Table | 0x0020 | Temperature sensor bad
FX_Warning_Table | 0x0040 | Communications error
FX_Warning_Table | 0x0080 | Cooling fan fault
FX_Sell_Status_Table | 0x0001 | AC input frequency too high
FX_Sell_Status_Table | 0x0002 | AC input frequency too low
FX_Sell_Status_Table | 0x0004 | AC input voltage too low
FX_Sell_Status_Table | 0x0008 | AC input voltage too high
FX_Sell_Status_Table | 0x0010 | Awaiting sell delay
FX_Sell_Status_Table | 0x0020 | Sell disabled
FX_Sell_Status_Table | 0x0040 | Battery voltage less than target
FX_Sell_Status_Table | 0x0080 | AC2 selected
FN_Status_Table | 0x0001 | AUX relay enabled
FN_Status_Table | 0x0002 | Charge parameters met
OB_Control_Status_Table | 0x0001 | Bulk Charging
OB_Control_Status_Table | 0x0002 | Float Charging
OB_Control_Status_Table | 0x0004 | Inverter AC Input Use
OB_Control_Status_Table | 0x0008 | Inverter Off
OB_Control_Status_Table | 0x0010 | Inverter Search Mode
OB_Control_Status_Table | 0x0020 | Inverter On
OB_Control_Status_Table | 0x0040 | Inverter Grid-Tie Enabled
OB_Control_Status_Table | 0x0080 | Inverter Charger Disabled
OB_Control_Status_Table | 0x0100 | Inverter Charger Auto Mode
OB_Control_Status_Table | 0x0200 | Inverter Charger Bulk and Float Mode
OB_Control_Status_Table | 0x0400 | EQ Charging